--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Australian/New Zealand Standard™

Electrical installations— Selection of cables

Part 1.2: Cables for alternating voltages up to and including 0.6/1 kV—Typical New Zealand installation conditions

AS/NZS 3008.1.2:1998

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

This Joint Australian/New Zealand Standard was prepared by Joint Technical Committee EL/1, Wiring Rules. It was approved on behalf of  the  Council  of  Standards Australia on 11 February 1998 and on behalf of the Council of Standards New Zealand on 12 February 1998. It was published on 5 May 1998.

The following interests are represented on  Committee   EL/1:

The Association of Consulting Engineers, Australia Australian Building Codes  Board

Australian Electrical and Electronic Manufacturers Association Canterbury Manufacturers Association, New Zealand Communications Electrical Plumbing Union,  Australia

DAS Interiors Australia

Electrical Contractors Association,  Qld

Electrical Contractors Association of New Zealand Electricity  Supply  Association  of  Australia Institute of Electrical Inspectors, Australia Institution of  Engineers, Australia

Insurance Council of Australia Ministry of  Commerce, New Zealand

National Electrical Contractors Association of Australia Regulatory authorities (electrical),  Australia

Telstra  Corporation, Australia

Review of Standards.  To  keep  abreast  of  progress  in  industry,  Joint  Australian/  New Zealand Standards are subject to periodic review and are kept up to date by the    issue of amendments or new editions as necessary. It is important therefore  that  Standards users ensure that they are in possession of the latest edition, and any amendments thereto.

Full details of all Joint Standards and related publications will be found in the Standards Australia and Standards New Zealand Catalogue of Publications; this information is supplemented each month by the magazines ‘The Australian Standard’ and ‘Standards New Zealand’, which subscribing members receive, and which give details of new publications, new editions and amendments, and of withdrawn  Standards.

Suggestions for improvements to Joint Standards, addressed to the head office of either Standards Australia or Standards New Zealand, are welcomed. Notification of any inaccuracy or ambiguity found in a Joint Australian/New Zealand Standard should be made without delay in order that the matter may be investigated and appropriate action taken.

This Standard was issued in draft form for comment as DR 96408 (in   part).

Australian/New Zealand Standard™

Electrical installations— Selection of cables

Part 1.2: Cables for alternating voltages up to and including 0.6/1 kV—Typical New Zealand installation conditions

First published as AS/NZS 3008.1.2:1998.

Published jointly by:

Standards Australia 1 The Crescent,

Homebush NSW 2140 Australia

Standards New Zealand

Level 10, Radio New Zealand House, 155 The Terrace,

Wellington 6001 New Zealand

ISBN 0 7337 1902 3

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	2

## PREFACE

This Standard was prepared by the Joint Standards Australia/ Standards New Zealand Committee EL/1, Wiring Rules, to supersede AS 3008.1—1989, Electrical installations— Selection of cables, Part 1:       Cables for alternating voltages up to and including 0.6/1 kV.

This Standard (Part 1.2) is applicable to New Zealand installation conditions where the nominal ambient air and soil temperatures are 30°C and 15°C, respectively. Part 1.1 is applicable to Australian installation conditions where the nominal  air  and  soil temperatures are 40°C and 25°C, respectively. Each Part is a complete  Standard  and requires no reference to the  other.

Part 2 will deal with cables for use with alternating voltages over 1 kV.

The objective of the Standard is to specify current-carrying capacity, voltage drop and short-circuit temperature rise of cables, to provide a method of selection for those types of electric cables and methods of  installation which are in  common use at  working voltages up to and including 0.6/1 kV at 50 Hz    a.c.

This Standard differs from the 1989 edition as   follows:

- Cables with a conductor operating temperature of 110°C have been added.

- Aluminium sheathed MIMS cables have been deleted, tables for copper sheathed MIMS cables have been revised and their sheath operating temperature has been changed to 100°C.

- Paper insulated cables have been  deleted.

- Voltage drop tables for tinned copper conductors have been    deleted.

- References have been added for aerial bundled   cables.

- Tables apply to New Zealand installation   conditions.

- Tables have been recalculated to IEC 287, Electric cables— Calculation of  the current rating (all Parts), based on conductor, insulation and sheath dimensions in   the relevant Australian/New Zealand Standards and New Zealand ambient temperatures, except as detailed in Clause 3.1.2. The current ratings for  insulated aerial cables are generally based on IEC 287 and on methods proposed by Dr V.T. Morgan of the CSIRO. The work carried out by Dr V.T. Morgan was sponsored by ESAA and AEEMA.

In the preparation of this Standard, reference was made to IEC 287 and acknowledgment     is made of the assistance received from that   source.

Statements expressed in mandatory terms in notes to tables and figures are deemed to be requirements of this  Standard.

The term ‘informative’ has been used in this Standard to define the application of the appendix to which it applies. An ‘informative’ appendix is only for information and guidance.

3	AS/NZS 3008.1.2:1998

## CONTENTS

Page

FOREWORD	8

SECTION 1   SCOPE AND GENERAL

  - SCOPE AND APPLICATION	9

  - ALTERNATIVE SPECIFICATIONS	9

  - REFERENCED AND RELATED DOCUMENTS	10

  - DEFINITIONS	11

SECTION 2   CABLE SELECTION PROCEDURE

  - GENERAL	12

  - SELECTION PROCESS	12

  - DETERMINATION	OF	MINIMUM	CABLE	SIZE	BASED	ON

CURRENT-CARRYING CAPACITY CONSIDERATIONS	12

  - DETERMINATION	OF	MINIMUM	CABLE	SIZE	BASED	ON

VOLTAGE DROP CONSIDERATIONS	13

  - DETERMINATION  OF  MINIMUM  CABLE  SIZE  BASED  ON   THE

SHORT-CIRCUIT TEMPERATURE CONSIDERATIONS	14

SECTION 3   CURRENT-CARRYING CAPACITY

  - RATINGS	15

  - TYPES OF CONDUCTORS	15

  - TYPES OF CABLE	16

  - INSTALLATION CONDITIONS	18

  - EXTERNAL INFLUENCES ON CABLES	21

SECTION 4   VOLTAGE DROP

  - GENERAL	64

  - DETERMINATION OF VOLTAGE DROP FROM MILLIVOLTS   PER

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AMPERE METRE	64

  - DETERMINATION OF VOLTAGE DROP FROM  CIRCUIT

IMPEDANCE	65

  - DETERMINATION OF VOLTAGE DROP FROM  CABLE

OPERATING TEMPERATURE	66

  - DETERMINATION OF VOLTAGE DROP FROM  LOAD

POWER FACTOR	67

  - DETERMINATION OF VOLTAGE DROP IN  UNBALANCED

MULTIPHASE CIRCUITS	68

SECTION 5   SHORT-CIRCUIT PERFORMANCE

  - GENERAL	88

  - FACTORS	GOVERNING	THE	APPLICATION	OF	THE

TEMPERATURE LIMITS	88

  - CALCULATION OF PERMISSIBLE  SHORT-CIRCUIT CURRENTS	89

  - INFLUENCE OF METHOD OF INSTALLATION	89

  - MAXIMUM PERMISSIBLE SHORT-CIRCUIT TEMPERATURES	90

AS/NZS 3008.1.2:1998	4

Page

APPENDICES

- EXAMPLES OF THE SELECTION OF CABLES TO SATISFY CURRENT-CARRYING CAPACITY, VOLTAGE DROP  AND

SHORT-CIRCUIT PERFORMANCE REQUIREMENTS	92

- RECOMMENDED CIRCUIT CONFIGURATIONS FOR  THE

INSTALLATION OF SINGLE-CORE CABLES  IN PARALLEL	101

LIST OF TABLES

1	LIMITING TEMPERATURES FOR  INSULATED CABLES	16

2(1)	SCHEDULE OF INSTALLATION METHODS FOR  CABLES DEEMED TO HAVE THE SAME CURRENT-CARRYING CAPACITY   AND

CROSS-REFERENCES TO APPLICABLE DERATING  TABLES—

UNENCLOSED IN AIR	28

2(2)	SCHEDULE OF INSTALLATION METHODS FOR  CABLES DEEMED TO HAVE THE SAME CURRENT-CARRYING CAPACITY   AND

CROSS-REFERENCES TO APPLICABLE DERATING  TABLES—

ENCLOSED	30

2(3)	SCHEDULE OF INSTALLATION METHODS FOR  CABLES DEEMED TO HAVE THE SAME CURRENT-CARRYING CAPACITY   AND

CROSS-REFERENCES TO APPLICABLE DERATING  TABLES—

BURIED DIRECT IN  THE GROUND	32

2(4)	SCHEDULE OF INSTALLATION METHODS FOR  CABLES DEEMED TO HAVE THE SAME CURRENT-CARRYING CAPACITY   AND

CROSS-REFERENCES TO APPLICABLE DERATING  TABLES—

ENCLOSED IN UNDERGROUND PIPES  AND DUCTS	33

- CURRENT-CARRYING CAPACITIES OF TWO  SINGLE-CORE

0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED   CABLES

WITH V-75, V-90, V-90HT, HFI-75-TP OR HFI-90-TP INSULATION     . .	34

- CURRENT-CARRYING CAPACITIES OF TWO  SINGLE-CORE

0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED CABLES WITH X-90, X-HF-90, R-EP-90, R-CPE-90, R-HF-90 OR   R-CSP-90

INSULATION	35

- CURRENT-CARRYING CAPACITIES OF TWO  SINGLE-CORE

0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED   CABLES

WITH R-HF-110, R-E-110 OR  X-HF-110 INSULATION	36

- CURRENT-CARRYING CAPACITIES OF THREE  SINGLE-CORE

0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED   CABLES

WITH V-75, V-90, V-90HT, HFI-75-TP OR HFI-90-TP INSULATION     . .	37

- CURRENT-CARRYING CAPACITIES OF THREE  SINGLE-CORE

0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED CABLES WITH X-90, X-HF-90, R-EP-90, R-CPE-90, R-HF-90 OR   R-CSP-90

INSULATION	38

- CURRENT-CARRYING CAPACITIES OF THREE  SINGLE-CORE

0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED   CABLES

WITH R-HF-110, R-E-110 OR  X-HF-110 INSULATION	39

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

5	AS/NZS 3008.1.2:1998

Page

- CURRENT-CARRYING CAPACITIES OF TWO-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING  NEUTRAL

SCREENED) CABLES WITH OR WITHOUT EARTH CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH V-75,   V-90,

HFI-75-TP OR HFI-90-TP INSULATION	40

- CURRENT-CARRYING CAPACITIES OF TWO-CORE 0.6/1  kV

INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED) CABLES WITH OR WITHOUT EARTH CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH X-90, X-HF-90, R-EP-90,   R-CPE-90,

R-HF-90 OR R-CSP-90 INSULATION	41

- CURRENT-CARRYING CAPACITIES OF TWO-CORE 0.6/1  kV

INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED) CABLES WITH OR WITHOUT EARTH CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH R-HF-110, R-E-110 OR   X-HF-110

INSULATION	42

- CURRENT-CARRYING CAPACITIES OF THREE-CORE  AND

FOUR-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED) CABLES WITH OR WITHOUT   EARTH

CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES  WITH

V-75, V-90, HFI-75-TP OR  HFI-90-TP INSULATION	43

- CURRENT-CARRYING CAPACITIES OF THREE-CORE  AND

FOUR-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED) CABLES WITH OR WITHOUT   EARTH

CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH X-90, X-HF-90, R-EP-90, R-CPE-90, R-HF-90 OR   R-CSP-90

INSULATION	44

- CURRENT-CARRYING CAPACITIES OF THREE-CORE  AND

FOUR-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED) CABLES WITH OR WITHOUT   EARTH

CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES  WITH

R-HF-110, R-E-110 OR  X-HF-110 INSULATION	45

- CURRENT-CARRYING CAPACITIES OF 0.6/1 kV   FLEXIBLE

CABLES	46

- CURRENT-CARRYING CAPACITIES OF  FLEXIBLE CORDS	47

- CURRENT-CARRYING CAPACITIES OF CABLES AND FLEXIBLE CORDS WITH R-S-150, TYPE 150 FIBROUS OR 150 TYPE    PTFE

INSULATION	48

- CURRENT-CARRYING CAPACITIES OF BARE  SINGLE-CORE

MINERAL-INSULATED COPPER-SHEATHED CABLES WITH  COPPER

CONDUCTORS— SHEATH TEMPERATURE: 100°C	49

- CURRENT-CARRYING CAPACITIES OF BARE MULTICORE MINERAL-INSULATED COPPER-SHEATHED CABLES  WITH

COPPER CONDUCTORS— SHEATH TEMPERATURE: 100°C	50

- CURRENT-CARRYING CAPACITIES OF AERIAL CABLES  WITH

COPPER CONDUCTORS	51

- CURRENT-CARRYING CAPACITIES OF AERIAL AND  ABC

CABLES WITH ALUMINIUM CONDUCTORS	53

- DERATING FACTORS FOR BUNCHED CIRCUITS OF   SINGLE-CORE

OR MULTICORE CABLES IN AIR OR IN WIRING ENCLOSURES   .    . .	55

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	6

Page

- DERATING FACTORS FOR CIRCUITS OF SINGLE-CORE CABLES INSTALLED IN TRAYS, RACKS, CLEATS, OR OTHER   SUPPORTS

IN AIR	56

- DERATING FACTORS FOR CIRCUITS OF MULTICORE CABLES INSTALLED IN TRAYS, RACKS, CLEATS OR OTHER   SUPPORTS

IN AIR	58

25(1)   DERATING FACTORS FOR GROUPS OF CIRCUITS  OF

SINGLE-CORE OR MULTICORE CABLES BURIED DIRECT IN   THE

GROUND— SINGLE-CORE CABLES	59

25(2) DERATING FACTORS FOR GROUPS OR CIRCUITS OF SINGLE-CORE OR MULTICORE CABLES BURIED DIRECT IN THE   GROUND—

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

MULTICORE CABLES	59

26(1) DERATING FACTORS FOR GROUPS OF CIRCUITS OF SINGLE-CORE OR MULTICORE CABLES INSTALLED IN WIRING   ENCLOSURES—

SINGLE CORE CABLES  ENCLOSED SEPARATELY	60

26(2) DERATING FACTORS FOR GROUPS OF CIRCUITS OF SINGLE-CORE OR MULTICORE CABLES INSTALLED IN UNDERGROUND WIRING ENCLOSURES— MULTICORE CABLES ENCLOSED SEPARATELY OR

MORE THAN ONE SINGLE-CORE CABLE PER   WIRING ENCLOSURE	60

27(1) RATING FACTORS FOR VARIATIONS IN AMBIENT TEMPERATURE FOR CABLES IN AIR OR HEATED CONCRETE SLABS AND    FOR

CABLES BURIED DIRECT IN GROUND OR IN UNDERGROUND WIRING ENCLOSURES— AIR AND CONCRETE SLAB

TEMPERATURES.	61

27(2) RATING FACTORS FOR VARIATIONS IN AMBIENT TEMPERATURE FOR CABLES IN AIR OR HEATED CONCRETE SLABS AND    FOR

CABLES BURIED DIRECT IN GROUND OR IN   UNDERGROUND

WIRING ENCLOSURES— SOIL TEMPERATURES	61

28(1) RATING FACTORS FOR VARIATIONS IN DEPTH OF LAYING FOR CABLES BURIED DIRECT IN THE GROUND AND FOR   CABLES

INSTALLED IN UNDERGROUND WIRING  ENCLOSURES—

SINGLE-CORE OR MULTICORE CABLES  BURIED DIRECT	62

28(2) RATING FACTORS FOR VARIATIONS IN DEPTH OF LAYING FOR CABLES BURIED DIRECT IN THE GROUND AND FOR   CABLES

INSTALLED IN UNDERGROUND WIRING  ENCLOSURES—

SINGLE-CORE AND MULTICORE CABLES IN  UNDERGROUND

WIRING ENCLOSURES	62

- RATING FACTORS FOR CABLES BURIED DIRECT IN GROUND AND FOR CABLES INSTALLED IN UNDERGROUND  WIRING

ENCLOSURES WHERE THE THERMAL RESISTIVITY OF   THE

SOIL VARIES FROM 1.2°C.m/W	63

- REACTANCE AT 50 Hz OF ALL CABLES EXCLUDING FLEXIBLE CORDS AND CABLES, MINERAL-INSULATED  METAL-SHEATHED

CABLES AND AERIAL CONDUCTORS	70

- REACTANCE AT 50 Hz OF FLEXIBLE CORDS   AND CABLES	71

- REACTANCE AT 50 Hz OF  MINERAL-INSULATED

METAL-SHEATHED CABLES	72

- REACTANCE AT 50 Hz OF SINGLE-CORE AERIAL   CONDUCTORS

WITH BARE OR  INSULATED CONDUCTORS	73

7	AS/NZS 3008.1.2:1998

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Page

- a.c. RESISTANCE AT 50 Hz OF   SINGLE-CORE CABLES	74

- a.c. RESISTANCE AT 50 Hz OF MULTICORE CABLES   WITH

CIRCULAR CONDUCTORS	75

- a.c. RESISTANCE AT 50 Hz OF MULTICORE CABLES   WITH

SHAPED CONDUCTORS	75

- a.c. RESISTANCE AT 50 Hz OF FLEXIBLE CABLES AND    CORDS

WITH COPPER CONDUCTORS	76

- a.c. RESISTANCE AT 50 Hz OF   MINERAL-INSULATED

METAL-SHEATHED CABLES	76

- a.c. RESISTANCE AT 50 Hz OF SINGLE-CORE AERIAL   CABLES

WITH BARE OR  INSULATED CONDUCTORS	77

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF   SINGLE-CORE

INSULATED AND SHEATHED COPPER CONDUCTORS, LAID   IN

TREFOIL	78

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF   SINGLE-CORE

INSULATED AND SHEATHED COPPER CONDUCTORS, LAID   FLAT

TOUCHING OR IN A  WIRING ENCLOSURE	79

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF   MULTICORE

CABLES WITH CIRCULAR COPPER CONDUCTORS	80

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF   SINGLE-CORE

INSULATED AND SHEATHED ALUMINIUM CONDUCTORS, LAID   IN

TREFOIL	81

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF   SINGLE-CORE

INSULATED AND SHEATHED ALUMINIUM CONDUCTORS,  LAID

FLAT TOUCHING	81

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF   MULTICORE

CABLES WITH CIRCULAR ALUMINIUM CONDUCTORS	82

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF   SINGLE-CORE

FLEXIBLE CABLES AND CORDS WITH COPPER   CONDUCTORS,

LAID IN TREFOIL	83

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF   MULTICORE

FLEXIBLE CABLES AND CORDS WITH COPPER CONDUCTORS  .    . .	84

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF SINGLE-CORE AND MULTICORE MINERAL-INSULATED METAL-SHEATHED  (MIMS)

CABLES, LAID IN TREFOIL	85

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF AERIAL   CABLES

WITH BARE OR INSULATED  COPPER CONDUCTORS	86

- THREE-PHASE VOLTAGE DROP AT 50 Hz OF AERIAL   CABLES

WITH BARE OR INSULATED  ALUMINIUM CONDUCTORS	87

- VALUES OF CONSTANT K FOR DETERMINATION   OF

PERMISSIBLE SHORT-CIRCUIT CURRENTS	89

- TEMPERATURE LIMITS FOR INSULATING MATERIALS  IN

CONTACT WITH CONDUCTORS	90

- TEMPERATURE LIMITS FOR OUTER SHEATH AND   BEDDING

MATERIALS	91

- TEMPERATURE LIMITS FOR CONDUCTOR AND  METALLIC

SHEATH MATERIALS AND COMPONENTS	91

AS/NZS 3008.1.2:1998	8

## FOREWORD

This Standard gives the sustained or continuous constant current which is sufficient to produce the maximum permissible conductor temperature under specified ambient conditions. The time taken to reach this  steady state  temperature will  vary depending on the type of cable and installation conditions. There will be many cable installations where, because of cable selection practices or demand patterns, the current is not sustained at the maximum specified in this Standard. Under these conditions care should be taken in the application of the correction factors included in Tables 22 to 26; it may be possible to    derive other appropriate correction factors for these   installations.

The contents of the Standard are a development of the limited provision of Appendix D to NZS 3000 and it is expected that AS/NZS 3000, currently under development, will have a modified and reduced Appendix and reference made to  this  Standard.  For  New  Zealand the requirements  of  NZECP 28  apply  and  this  will  be  updated  to  reflect  changes  in AS 3008.1, or will be  withdrawn.

© Copyright	STANDARDS AUSTRALIA/ STANDARDS NEW  ZEALAND

Users of Standards are reminded that copyright subsists in all Standards Australia and Standards New Zealand publications and software. Except  where  the  Copyright  Act  allows  and  except  where  provided  for  below  no  publications   or   software   produced   by   Standards Australia or Standards New Zealand may be reproduced, stored in a retrieval system in any form or transmitted by any means without prior permission in writing from Standards Australia or Standards New  Zealand.  Permission  may  be  conditional  on  an  appropriate royalty payment. Australian requests for permission and information on commercial software royalties should be directed to       the head office of Standards Australia. New Zealand requests should be directed to Standards New Zealand.

Up to 10 percent of the technical content pages of a Standard may be copied for use exclusively in-house by purchasers of the  Standard without payment of a royalty or advice to Standards Australia or Standards New Zealand.

Inclusion of copyright material in computer software programs is  also permitted without royalty  payment provided  such programs are used exclusively in-house by the creators of the    programs.

Care should be taken to ensure that material used is from the current edition of the Standard and that it is updated whenever the Standard        is amended or revised. The number and date of the Standard should therefore be clearly identified.

The use of material in print form or in computer software programs to be used commercially, with or without payment, or in commercial contracts is subject to the payment of a royalty. This policy may be varied by Standards Australia or Standards New Zealand at any time.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

9	AS/NZS 3008.1.2:1998

## STANDARDS AUSTRALIA/ STANDARDS NEW ZEALAND

Australian/ New Zealand Standard

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Electrical installations— Selection of cables

## Part 1.2: Cables for alternating voltages up to and including 0.6/1 kV— Typical New Zealand installation conditions

## S  E  C  T  I O N	1	S  C  O P E	A N D	G  E  N  E  R  A L

### SCOPE AND APPLICATION

    - Scope This Standard sets out a method for cable selection for those types  of  electrical cables and methods of installation which are in common use at working voltages up to and including 0.6/1 kV at 50 Hz    a.c.

Three criteria are given for cable selection, as    follows:

- Current-carrying capacity.

- Voltage drop.

- Short-circuit temperature rise.

This Standard provides sustained current-carrying capacities and voltage drop values for those types of electrical cable and installation practices in  common use in  New Zealand.    A significant amount of explanatory material is also provided on the application of rating factors which arise from the particular installation conditions of a  single circuit or groups   of circuits. Also, provided in Section 5 is information on cable selection based on short-circuit temperature limits.

NOTE: A number of worked examples on cable selection are included in Appendix A.

This Standard does not take into account the effects that may occur owing to temperature rise at the terminals of equipment and reference is necessary to NZS 3000 and  the  individual equipment Standards.

    - Application   This Standard is intended to apply to installations made or carried     out after the date of publication, but it is recommended that it not be  applied  on  a  mandatory basis until 6 months after the date of publication. However, if work on an installation is commenced before publication of this edition, the inspecting authority may grant permission for the installation to be carried out in accordance with the superseded edition.

  - ALTERNATIVE SPECIFICATIONS NZS 3000  gives  current-carrying capacities for a limited number of cable installation conditions. These conditions are included in this Standard but, in some cases where recalculations have  been  performed,  the  tabulated values differ slightly between the Standards. Where this occurs  the  current-carrying capacity given in this Standard is considered to be more accurate, but either value is acceptable for the application of any  appropriate  requirements  of NZS 3000,  e.g. maximum current rating of a circuit-protective   device.

Where the type of cable or method of installation is not specifically covered in the tables     of this  Standard, current-carrying capacities obtained from  alternative specifications such as ERA Report 69-30 may be   employed.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	10

ERA Report 69-30, particularly Part III, gives information on the following areas which    are not covered by this  Standard:

- The d.c. current-carrying capacities of two single-core cables and one  two-core  cable.

- The current-carrying capacity of armoured single-core   cables.

- Group rating factors for underground cables laid in tier    formation.

Current-carrying capacities may also be determined by calculation using IEC 287 and appropriate cable data.

The subject of assigning a current-carrying capacity to a  cyclically  or  intermittently  loaded cable is not covered in this Standard as it normally relates to HV cable installation. However, reference may be made to ERA Report F/T 186 for information on the determination of such cable ratings by   calculation.

### REFERENCED AND RELATED  DOCUMENTS

    - Referenced documents	The following documents are referred to in   this Standard: STANDARDS

AS

1125	Conductors in insulated electric cables and flexible   cords

NZS

3000	Electrical  installations— Buildings,  structures  and  premises  (known    as  the NZS Wiring Rules)

NZECP

28	New Zealand electrical code of practice for selection and installation of cables

IEC

287	Electric cables— Calculation of the current rating (all  Parts)

ERA REPORTS

69-30	Current rating standards for distribution  cables

Part III:   Sustained current ratings for PVC-insulated  cables

Part V: Sustained current ratings for armoured cables with thermo-setting insulation

F/T

186	Methods for the calculation of cyclic rating factors and emergency loading for cables laid direct in the ground or in   ducts

    - Related documents	Attention is drawn to the following   related documents: AS

1531	Conductors— Bare overhead— Aluminium and aluminium alloy

1746	Conductors— Bare overhead— Hard-drawn copper

3147	Approval	and	test	specification — Electric	cables — Thermoplastic insulated— For working voltages up to and including 0.6/1   kV

3158	Approval and test specification— Electric cables— Glass fibre   insulated— For working voltages up to and including 0.6/1   kV

3178		Approval	and	test	specification — Electric	cables— Silicone	rubber insulated— For working voltages up to and including 0.6/1   kV

3560	Electric cables— XLPE insulated— Aerial bundled— For working  voltages up to and including 0.6/1  kV

COPYRIGHT

11	AS/NZS 3008.1.2:1998

AS/NZS

3116	Approval and test specification— Electric cables— Elastomer    insulated— For working voltages up to and including 0.6/1   kV

3155	Approval   and   test   specification— Electric   cables— Neutral screened— For working voltages of 0.6/1  kV

3187	Approval and test specification— Mineral-insulated  metal-sheathed cables 3191	Approval and test specification— Electric flexible  cords

3198	Approval   and   test   specification— Electric   cables— XLPE  insulated— For working voltages up to and including 0.6/1   kV

IEC

724	Guide  to  the  short-circuit  temperature  limits  of  electric  cables  with a  rated voltage not exceeding 0.6/1.0  kV

  - DEFINITIONS For the purpose of this Standard, the definitions in NZS 3000,  NZECP 28 and those below  apply.

    - Ambient temperature—the temperature of the medium in the immediate neighbourhood of the installed  cable—

- including any increase in temperature due to materials or equipment to which the cables are connected, or are to be connected;   but

- excluding any increase in temperature which may be  due  to  the  heat  arising from  the cables at that  point.

    - Continuous loading — a continuous constant current (100% load factor) just sufficient to produce asymptotically the maximum conductor temperature, the surrounding ambient conditions being assumed  constant.

    - Ladder support—a support in which the impedance of air flow around the cable     is not greater than 10%, i.e. supporting metalwork under the cable occupies less than 10%   of the plan  area.

    - Perforated tray—a tray having not less than 30% of its surface area removed by   the perforation.

    - Route length—the distance measured along a run of wiring from the origin of the circuit to the point of consideration, e.g. the distance measured between a switchboard and    a motor.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	12

S  E  C  T  I O N	2	C A B L E	S E L E C T I O N	P R O C E D U R E

  - GENERAL The cable selection procedures set out in this  Section  detail  the guidelines to be followed to determine the minimum size of cable required to satisfy a particular installation condition.

  - SELECTION PROCESS  The  following three  main  factors influence the  selection of a particular cable to satisfy the circuit   requirements:

- Current-carrying capacity—dependent upon the method of installation and the presence of external influences, such as thermal insulation, which restrict the  operating temperature of the  cable.

- Voltage drop—dependent upon the impedance of  the cable, the magnitude of  the  load current and the load power   factor.

- Short-circuit temperature limit—dependent upon energy produced during the short-circuit condition.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

The minimum cable size will be the smallest cable that satisfies the three requirements. However, with experience it will become apparent that the different nature of installations will determine which of the requirements predominate. In general, the current-carrying capacity requirement will be the most demanding in the relatively shorter route lengths of domestic premises and the like where factors such as semi-enclosed rewirable fuse protection, cable grouping, and thermal insulation occur. On  the other hand the voltage   drop limitation is usually the deciding factor for longer  route  lengths  which  are  not subject to the factors mentioned above. The need to increase cable size to meet the short-circuit temperature rise requirements will only occur in special situations for the voltage ratings of the cables covered by this   Standard.

  - DETERMINATION OF MINIMUM CABLE SIZE BASED ON CURRENT- CARRYING CAPACITY CONSIDERATIONS To satisfy the current-carrying capacity requirements of a circuit it is necessary to take into account a number  of  factors,  as  follows:

- Determine the current requirements of the   circuit.

NOTES:

  - NZS 3000 makes requirements concerning the relationship between the  current required  by the load connected to the circuit, the type and current rating of the overcurrent protective device, and the current-carrying capacity of the cable. Such factors will invariably determine the minimum current requirements for the application of this  Standard.

  - Where rewirable fuses form the circuit-protection, NZS 3000 makes provision for a  derating factor to be applied to the current-carrying capacity of cable determined from   this Standard. This derating factor is necessary because of the desire to limit  the  maximum permissible temperature rise under overload   conditions.

- Determine the method of cable installation to be used, as follows:

- For a single circuit, determine if the method of installation requires the application of a derating factor selected from Tables 22, 23 or 24. Where applicable, divide the value of current determined in Step (a) by the derating factor so determined.

COPYRIGHT

13	AS/NZS 3008.1.2:1998

- For a group of circuits, determine if the method of installation requires the application of a derating factor selected from Tables 22 to 26. Where applicable, divide the value of current determined by Step (a) by the derating factor so determined.

NOTE: Tables 2(1), 2(2), 2(3) and 2(4) provide a guide to the installation  methods  and derating factors applicable to the common elastomer or thermoplastic-insulated    cables.

- Determine the environmental conditions in the vicinity of the cable installation.  Where applicable, divide the value of current determined in Step (b) by—

- the ambient air or soil temperature rating factor selected from Tables 27(1)  and 27(2);

- the depth of laying rating factor selected from Tables 28(1) and 28(2); and

- the soil thermal resistivity rating factor selected from Table    29.

- The resulting value of current represents the minimum current-carrying capacity required of the circuit. Reference is then made to the tables of current-carrying  capacity for the different cable types, i.e. Tables 3 to 21. Taking into account the method of installation employed, the smallest conductor size which has a tabulated current-carrying capacity equal to or in excess of this predetermined minimum value will be considered to be the minimum cable size satisfying the current-carrying capacity requirement.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

DETERMINATION OF MINIMUM CABLE SIZE  BASED  ON VOLTAGE DROP CONSIDERATIONS To satisfy the voltage drop limitations of a circuit, it is necessary to take into account the current required by the load and the route length of the circuit, as follows:

- Determine the current (I) requirements of the   circuit.

- Determine the route length (L) of the   circuit.

- Determine the maximum voltage drop (Vd) permitted on the circuit run.

NOTE: NZS 3000 generally limits the fall in  voltage from the point of  supply to  any point    of an installation to 5% of the nominal voltage at the consumers’ terminals.

- Determine the voltage drop (Vc) in millivolts per ampere metre (mV/A.m) using Equation 4.2(1) and the values of I, L and Vd determined in Steps (a), (b) and (c).

- Refer to the tables of voltage drop (mV/A.m) for the different  cable  types,  i.e.  Tables 40 to 50. Taking into account the  method  of installation,  maximum conductor operating temperature and load power factor, the smallest conductor size which has a  tabulated voltage drop (mV/A.m) value nearest to, but not exceeding,   the value determined in Step (d) will be considered to be the minimum cable size satisfying the voltage drop  limitation.

This simplified method gives an approximate but  conservative  solution  assuming  maximum cable operating temperatures and the  most  onerous relationship between load and cable power factors. A more accurate assessment can be  made  of  the  actual voltage drop (Vd) using  the appropriate equation of  Clause 4.5, the  cable reactance determined from Tables 30  to  33, the cable a.c. resistance determined from Tables 34  to  39  using   the

approximate conductor operating temperature assessed from Equation 4.4(1), and the load power factor.

NOTES:

- If the value of voltage drop assessed using the appropriate equation of Clause 4.5 is significantly lower than the equivalent value determined using the simplified  method suggested in Steps (a) to (e), consideration should  be  given  to  the  calculation  of  voltage drop for the next smaller cable   size.

COPYRIGHT

AS/NZS 3008.1.2:1998	14

- Because of the need to make an initial set of assumptions relating to cable size,  the  calculation method of Clause 4.5 will normally only be of use to check the accuracy of the simplified method or to check the voltage drop on an existing or known cable installation.

  - DETERMINATION OF MINIMUM CABLE SIZE BASED ON THE SHORT-CIRCUIT TEMPERATURE CONSIDERATIONS To satisfy the short-circuit temperature limit it is necessary to take into account the energy producing the temperature rise (I2t) and the initial and final temperatures, as    follows:

- Determine the maximum duration and value of the prospective short-circuit current.

- Determine the initial and final conductor temperatures and select  an  appropriate  value of the constant (K) from Table   51.

- Calculate the minimum cross-sectional area of the cable using Equation 5.3(1). This cable size represents the minimum size required to satisfy  the  short-circuit temperature rise requirements.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

15	AS/NZS 3008.1.2:1998

S E C T I O N    3      C U R R E N T - C A R R Y I N G    C A P A C I T Y

### RATINGS

    - General  The provisions of this Section apply to the selection of conductor sizes  with regard to current-carrying  capacity.

Clauses 3.2 to 3.5 stipulate conductor and cable requirements and installation conditions     in order that the subsequent tables of current-carrying capacity may be applied.

Tables 2(1) to 2(4) give guidance to the appropriate table of current-carrying capacity for different installation methods for the common types of cable insulant covered by Tables 3    to 14. A specific installation condition is defined  and  illustrated  and  alternative installation conditions deemed to have the same current-carrying capacity are also given. Attention is drawn to tables of rated current-carrying capacity where the  standard installation conditions of Clause 3.4 are   varied.

Tables 3 to 21 give the current-carrying capacities for the variety of different cable types described in Clause  3.3.

    - Basis The values for current ratings given in Tables 3 to 14 have been calculated using the method described in IEC 287 except for 75°C and 90°C rated cables enclosed in conduit in air or partially surrounded by thermal   insulation.

NOTE: The parameters for calculating current ratings in PVC  conduits  in  IEC 287  are  still  under consideration and considerable disparity was noted between values calculated using available parameters and those previously published in the 1989 edition as well as other International Standards.

It has therefore been decided in these cases to leave the values previously assigned in the 1989 edition even though in some cases these appear to be higher than would normally be justified.    The ratings, however, for all other cables have been compared with international data  and  confirm the validity of using the IEC 287   method.

When IEC 287 is suitably amended then it is proposed to undertake a  revision of this Standard     to correct these  anomalies.

Furthermore it should be noted that the current ratings for 110°C rated  cables  enclosed  in  conduit in air assume the use of metallic conduit. If non-metallic conduits are used then these ratings are not  applicable.

### TYPES OF CONDUCTORS

    - Conductor material The current-carrying capacities are based on conductors of high-conductivity copper and aluminium in sizes, strandings  and  resistances  complying with AS 1125.

    - Insulation material operating temperatures The sustained current-carrying capacities are based on the ‘normal use’ temperatures specified in Column 2 of Table 1. Where the ‘maximum permissible’ temperature in Column 3 of Table 1 is greater than the ‘normal use’ temperature, the ‘maximum permissible’ temperature  may  only  be  used under the conditions described in Note 2 to Table 1 for thermoplastic cables and in Note 3     to Table 1 for MIMS  cables.

NOTE: Where cables are consistently operating substantially below the limiting temperature of Table 1, the heat losses (I2R) and voltage drop (IZ) will also be reduced. These features could       be relevant in determining the optimum economic design of a circuit.

COPYRIGHT

AS/NZS 3008.1.2:1998	16

### TYPES OF CABLE

    - Sheathed and unsheathed thermoplastic, elastomer and XLPE   cables

      - General The current-carrying  capacity  of sheathed  and  unsheathed thermoplastic, elastomer  or  XLPE  insulated  cables  shall  be  determined  from  Tables 3  to 14.

      - Method of installation  The  current-carrying capacity of  a  given  cable  depends  on the method of installation. Tables 2(1) to 2(4) provide a schedule of the installation methods applicable to sheathed and unsheathed elastomer or thermoplastic cables whose current-carrying capacities are given in Tables 3 to 14. Tables 2(1) to 2(4) also  draw attention to the different methods of installation which may be assigned the same current-carrying capacity and refers to tables of derating factors applicable  where  one  circuit is run in close proximity to another circuit or circuits.

### Flexible cords and  cables

      - Used for fixed wiring The determination of current-carrying capacity of flexible cords and cables used for fixed wiring shall be as follows:

- Not subject to flexing The  current-carrying capacity of  flexible cords  and  cables used as fixed wiring which are not subject to flexing in normal use shall  be determined from values for other cables of the corresponding insulant type as given   in Tables 3 to  14.

NOTE: The appropriate rating factors applicable to Tables 3 to 14 are applicable when the current-carrying capacity of flexible cords and cables  is  determined  in  accordance  with  Item (a).

- Subject to flexing  The  current-carrying capacity of  flexible cables and  cords  used  as fixed wiring but which are subject to flexing in normal use, shall be determined from Tables 15 or  16.

### TABLE	1

LIMITING TEMPERATURES FOR INSULATED  CABLES

| 1 | 2 | 3 |
| --- | --- | --- |
| Type of cable insulation | Operating temperatures of conductors, °C (see Note 1) |  |
|  | Normal use | Maximum permissible |
| Thermoplastic (see Note 2) |  |  |
| V-75 and HFI-75-TP | 75 | 75 |
| V-90 and HFI-90-TP | 75 | 90 |
| V-90HT | 75 | 105 |
| Elastomer |  |  |
| R-EP-90, R-CPE-90, R-HF-90 and R-CSP-90 | 90 | 90 |
| R-HF-110 and R-E-110 | 110 | 110 |
| Cross-linked polyethylene (XLPE) |  |  |
| X-90 and X-HF-90 | 90 | 90 |
| X-HF-110 | 110 | 110 |
| Mineral-insulated | 100 (sheath) | 250 (sheath) |
| Copper sheathed (MIMS) (see Note 3) |  |  |
| High temperature (see Note 4) |  |  |
| R-S-150 elastomer | 150 | 150 |
| Type 150 fibrous or polymeric | 150 | 150 |
| Type 200 fibrous or polymeric | 200 | 200 |

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

17	AS/NZS 3008.1.2:1998

NOTES:

- The temperature limits specified in Table 1 relate to the sustained current-carrying capacity and  do  not  represent the maximum permissible temperatures permitted under short-circuit conditions. A guide to the acceptable short-circuit temperature limits is  given in  Section  5.

- The current-carrying capacities for thermoplastic cables, including flexible cords used as  fixed  wiring,  insulated with V-90 and V-90HT PVC compounds have been based on a conductor operating temperature of 75°C because of the likelihood of thermal deformation of these cable types in the temperature range 90  to  105°C. Cables may be operated in that temperature range when incorporated as equipment wiring and not exposed to mechanical damage, e.g. in certain types of luminaires and heating appliances. Cables totally surrounded by  thermal insulation may be  considered not exposed to  mechanical   damage.

- The current-carrying capacities for MIMS cables are based on an operating temperature of 100°C for  the  external surface of either bare metal-sheathed cables or served cables. Higher  continuous  operating  temperatures are permissible for bare metal-sheathed cables, particularly stainless steel sheathed cables, dependent upon factors such as the   following:

  - The suitability of  the cable terminations and   mountings.

  - The location of the cable away from combustible    materials.

  - The location of the cable away from areas where there is a reasonable chance of persons  touching the exposed surface.

  - Other environmental and external  influences.

- The current-carrying capacities given in Table 17 for cables insulated with high temperature elastomer, polymeric or fibrous materials are based on cables operating at temperatures of 150°C in  an  ambient  temperature of 30°C and where the hot cable surfaces are acceptable. However, the  cables  are  generally installed in  areas of  high ambient temperature, such as  equipment wiring, and it  will be  necessary to apply    an  appropriate temperature correction factor from Table   27.

The current-carrying capacities for fibrous and polymeric (PTFE)  type  cables  and  cords  suitable  for  operation at 200°C are not given in this Standard. As an alternative to the use of the relatively conservative  values given in Table 17, advice may be sought from cable manufacturers.

- Cables with an operating temperature of 110°C should only be connected to equipment suitable for this temperature. Consideration should also be given to the voltage drop at this operating temperature.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Other than fixed wiring The determination  of current-carrying  capacity  of  flexible cords and cables used for other than fixed wiring shall be as follows:

- General Except as provided in Item (b), the current-carrying capacity of  flexible  cords  and   cables   not   used   as   fixed   wiring   shall   be   determined   from  Tables 15 and  16.

- Connection of appliances    Where a flexible cord   is—

  - used for the connection of an appliance to the fixed wiring by means of a      plug and socket;  and

  - the appliance comes within the scope of associated   Standards;

the current-carrying capacity shall be determined from the appropriate    Standard.

    - Mineral-insulated metal-sheathed (MIMS) cables The current-carrying capacity  of bare or served copper MIMS cables shall be determined from Tables 18 and 19.

NOTE: Current-carrying capacities are not given in  this Standard for polyethylene served or   other forms of MIMS cable used for heating purposes, such as trace heating, tank heating or     floor warming.

    - Aerial cables The current-carrying capacity of aerial cables shall be determined  from Tables 20 and 21. See Clause 3.3.5 for the determination of the current-carrying capacity of neutral-screened aerial  cables.

    - Neutral-screened cables The current-carrying capacity of neutral-screened cables shall be determined from Tables 9 to 14, as appropriate to the number of cable cores and method of installation. However, the current-carrying capacity of neutral-screened aerial cables shall be determined as  follows:

- For two-core neutral-screened cable   . . . . . . . . . . . .     Columns 8  to  10  of Table

20	or	Table	21,	as appropriate.

COPYRIGHT

AS/NZS 3008.1.2:1998	18

- For three- or four-core neutral-screened cable   . . . . .      Columns  11  to  13  of Table

20	or	Table	21,	as appropriate.

    - High  temperature  elastomer,  polymeric  or fibrous  cables  and   flexible  cords The current-carrying capacity of R-S-150 elastomer insulated cables, Type 150 heat-resisting fibrous insulated cables and Type  150  PTFE  insulated flexible cords  shall be determined from Table  17.

    - Other cable types This Standard provides current-carrying capacities for types of cables that are considered to be in common use. For cables not included in this Standard, cable manufacturers should be consulted for recommendations on the current-carrying capacity and acceptable methods of  installation.

### 3.4    INSTALLATION CONDITIONS

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

3.4.1 General The current-carrying capacity of a cable is dependent on the method of installation to maintain the temperature of the cable within its operating limits. Different methods of installation vary the rate at which the heat generated by the current flow is dissipated to the surrounding  medium.

Specific conditions of installation are laid down in Clauses 3.4.2 to  3.4.5  for  cables installed with or without wiring enclosures in air, in the ground or embedded in building materials. These conditions have been used to derive the current-carrying capacities tabulated in Section 3. Where a  number of installation conditions exist along a  cable run    or variations to the specific conditions occur, reference shall be made to Clauses 3.4.6 and

3.5 respectively.

    - Cables installed in air For cables installed in free air, the  current-carrying capacities shall be based on the following conditions of installation and operation:

- Ambient temperature    An ambient air temperature of  30°C.

- Unenclosed cables    Cables installed as  follows:

  - Directly in air and, except for flexible cables  as  mentioned  in  Note  2  to  Table 1 and aerial cables, not exposed to direct sunlight and where they are—

    - lying on a horizontal  surface;

    - lying across ceiling  joists;

    - supported on perforated or unperforated cable trays, ladders, hangers or racks;

    - clipped at intervals to a vertical or horizontal surface, such as a wall or beneath a ceiling;

    - suspended from a catenary  wire;

    - lying in the bottom of open trunking;   or

    - in an enclosure such as a   switchboard.

  - Directly embedded beneath the surface of plaster, cement render or    masonry.

NOTE: Table 2(1) contains a reference to the appropriate current-carrying capacity table for cables installed unenclosed in  air.

- Enclosed cables    Cables installed as  follows:

  - In metallic or non-metallic wiring enclosure   in—

    - free air;

    - a ventilated or enclosed  trench;

COPYRIGHT

19	AS/NZS 3008.1.2:1998

    - a concrete slab on or above the surface of the ground; or

    - a concrete, plaster, cement rendered or masonry   wall.

  - In closed trunking.

  - In an enclosed trench with removable   covers.

  - Directly buried in  concrete.

NOTES:

- Table 2(2) contains a reference to the appropriate  current-carrying  capacity  table  for  enclosed cables installed in  air.

- Where an otherwise unenclosed cable run includes short lengths of wiring enclosure which    do not restrict the free circulation of air, the current-carrying capacity for unenclosed conditions may be assigned to the cable run provided that the following are complied with:

  - The total above-ground sections do not exceed half the length of the cable run or 6 m, whichever is the shorter  dimension.

  - The wiring enclosure is not surrounded by thermal   insulation.

  - The wiring enclosure is of adequate size to permit free air circulation to  dissipate any heat arising from the enclosed cables. This would be satisfied if the wiring enclosure—

    - has a  bore area not less than twice the total cross-sectional area of the enclosed   live cables;

    - is arranged in a  substantially vertical direction;  and

    - has an open upper end or other means which will not restrict the escape of hot air    to the surroundings.

- Selection of wiring enclosure material needs to take into account the highest sheath  temperature of the  cable.

    - Cables installed in thermal insulation For cables installed in  thermal insulation  the current-carrying capacities shall be based on the  following conditions of  installation  and operation:

- Ambient temperature	An  ambient  temperature  of  the  air  surrounding the thermal insulation of 30°C.

- Unenclosed cables    Cables installed without further  enclosure—

  - lying on a horizontal  surface;

  - lying across ceiling  joists;

  - supported on perforated or unperforated cable trays, ladders,  hangers  or  racks;

  - clipped at intervals to a vertical or horizontal surface such as  a  wall  or  ceiling joist; or

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

lying in the bottom of open   trunking.

- Enclosed cables    Cables installed in—

  - metallic or non-metallic wiring enclosure;  or

  - closed trunking or  ducts.

- Bulk thermal insulation    Bulk thermal insulation installed as   follows:

  - Materials	Building   materials   installed   to   provide   a  thermal  insulation including—

    - fibreglass or rockwool  batts;

    - cellulose fibre, paper, cork, seagrass or similar organic materials which are normally installed in a loose-fill form;   or

COPYRIGHT

AS/NZS 3008.1.2:1998	20

    - expanded synthetic foams such as polystyrene ureaformaldehyde or polyurethane which may be installed by pumping or injection as a wet foam.

NOTE: Reflective foil laminates are not considered to be bulk thermal insulation.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Completely surrounded installation An installation method  where  bulk thermal insulation surrounds, and is in contact with, unenclosed or enclosed cables.

  - Partially surrounded installation  An installation  method  where  bulk  thermal insulation is prevented from completely surrounding unenclosed or enclosed cable, such as where an unenclosed or enclosed cable is clipped to a structural member or is lying on a   ceiling.

NOTE: Table 2(2) contains a reference to the appropriate current-carrying  capacity  table  for cables installed in thermal  insulation.

    - Cables buried direct in the ground For cables buried direct in the ground, the current-carrying capacities shall be based on the following conditions of installation and operation:

- Ambient temperature    An ambient soil temperature of   15°C.

- Depth of laying	A depth of laying of 0.5 m measured from the ground surface to the centre of a cable, or to the centre of a trefoil group of cables.

- Thermal resistivity of soil    A soil thermal resistivity of   1.2°C.m/W.

- Spacing of cables    Cables are spaced as  follows:

  - Single-core cables	Either—

    - three single-core cables laid touching throughout in trefoil formation;   or

    - two or three single-core cables laid touching in flat    formation.

  - Multicore cables	Multicore cables laid  singly.

NOTE: Table 2(3) contains a reference to the appropriate current-carrying  capacity  table  for cables buried direct in the  ground.

    - Cables installed in underground wiring enclosures For cables installed in underground wiring enclosures, the current-carrying capacities shall be based on the following conditions of installation and  operation:

- Ambient temperature    An ambient soil temperature of   15°C.

- Depth of laying   A  depth of laying of 0.5 m  measured from the ground surface to   the centre of a wiring enclosure, or to the centre of a trefoil group of  wiring enclosures.

- Thermal resistivity of soil    A soil thermal resistivity of   1.2°C.m/W.

- Spacing of wiring enclosures    Wiring enclosures shall be spaced as    follows:

  - Single-core cables in separate wiring enclosures   with—

    - two ducts side by side touching;   or

    - three ducts in trefoil, or in flat formation   touching.

  - Single-core cables as a circuit in a single wiring    enclosure.

  - Multicore cable in a single wiring   enclosure.

NOTE: Table 2(4) contains a reference to the appropriate current-carrying  capacity  table  for cables installed in underground wiring  enclosures.

COPYRIGHT

21	AS/NZS 3008.1.2:1998

    - Variation of installation conditions along cable run In situations where  one method of installation is used for part of a cable run and other methods for the remainder,  the current-carrying capacity of the cable run shall be limited to the  lowest  value  of  current determined for each method of installation employed, unless precautions are taken which avoid cable  overheating.

NOTES:

      - An example of appropriate precautions is where long runs of cable  buried  direct  in  the  ground are enclosed in  wiring enclosures when passing beneath roadways and the like. The  use of selected backfill materials over the enclosed cables can  improve the  conduction  of  heat away from the cables and as a consequence higher current-carrying capacities, in  the order of that for buried direct cables, can be sustained by  the  short  lengths  of  enclosed cables.

      - Note 2 to Clause 3.4.2(c) describes a situation where a short length of suitably arranged enclosure may be disregarded for the assignment of a current-carrying capacity to  an otherwise unenclosed cable run in  air.

      - Attention is drawn to the connection of equipment to an underground cable run by means of short lengths of enclosed or unenclosed cables in air. The current-carrying capacity assigned  to the underground portion of the cable run may be assigned to the  above-ground portion  where the prevailing installation conditions maintain the final operating temperature of the cable within the limits given in Table   1.

### EXTERNAL INFLUENCES ON  CABLES

    - Application of rating factors The current-carrying capacity of a cable will be affected  by  the  presence  of  certain  external  influences  as  detailed  in  Clauses  3.5.2   to

3.5.8. Under such conditions the current-carrying capacity given in Tables 3 to 21 shall be corrected by the application of an appropriate rating factor  or  factors  obtained  from Tables 22 to  28.

### Effect of grouping of  cables

      - General The current-carrying capacities given in Tables 3 to 21 relate to single circuits.

Where a number of circuits are installed in the same group in free air, on a surface, buried direct in the ground or within the same sheath or wiring enclosure, in such a  way that       they are not independently cooled by the ambient air or the  ground,  the  appropriate derating factor shall be as given in Tables 22 to 26.

Specific guidance on the use of Tables 22 to 26 is given in Clauses 3.5.2.3 to 3.5.2.7 and Table 2.

NOTES:

        - The derating factors have been calculated on the basis of sustained operation of all cables  within the group. In most instances the loading on all cables in the group will not occur simultaneously and as a result actual factors may vary from those in Tables 22 to 26. Actual values would need to be calculated according to    loading.

        - Where cables of different temperature rating are grouped, they should be rated at the rating appropriate to the lowest temperature cable, unless adequate spacing is provided in  accordance with Figure  1.

      - Installation conditions which avoid derating   The derating factors of Tables 22     to 26 are not applicable to the following conditions of grouped cables:

- MIMS cables MIMS cables without serving unless  other  types  of cables  are installed in close proximity or within the same  wiring  enclosure.  The  higher operating temperature achieved by grouping will not affect the mineral insulation of the unserved cable. However, care must be taken that the cable environment and  means of support can withstand the higher   temperatures.

NOTE: See Note 3 to Table   1.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	22

- Limited length of grouping Groups of cables such as  at  a  switchboard  entry, provided that the length of wiring enclosure does not    exceed—

  - for conductor sizes smaller than 300 mm2 for aluminium   and

smaller than 150 mm2 for copper   . . . . . . . . . . . . . . . . . . . . . . . . . . .  1 m;

  - for conductor sizes of 300 mm2 or larger for aluminium    and

150 mm2 or larger for copper  . . . . . . . . . . . . . . . . . . . . . . . . . . . .  3 m; or

  - half the length of the cable; whichever is the shorter  dimension.

- Groups of circuits in free air Groups of circuits installed unenclosed under the conditions and circuit arrangements depicted in Figure   1.

- Cables operating below current-carrying capacity Cables which, as a result of the conditions of operation of  the installation or cable selection practices, are operating   at less than 35% of its current-carrying capacity (see Figure 1, Note 3).

      - Cables run horizontally For cables installed horizontally the  following  shall  apply:

- Unenclosed on cable tray, ladder support,  rack  hanger  or cleat  Where  a  single-core or multicore cable is installed horizontally in close proximity to  a  cable  or cables of another circuit  and—

  - it is on perforated or unperforated trays, ladder supports, racks, hangers or cleats; and

  - it is either—

    - touching the other cable or cables;   or

    - in terms of its spacing from the other cable or cables, less than that specified in Clause 3.5.2.2(c) and Figure   1;

the appropriate derating factor shall be as given in Table 23 or Table 24.

- Enclosed, fixed to a surface, or bunched in free  air  Where  a  single-core  or multicore cable is installed horizontally in close proximity to a cable or cables of another circuit—

  - within a wiring  enclosure;

  - on a surface, wall, floor or ceiling, spaced or    touching;

  - bunched in free air;  or

  - suspended from a  catenary;

the appropriate derating factor shall be as given in Table 22.

      - Cables run vertically Where a cable is installed vertically, the appropriate current-carrying capacities and derating factors shall   be—

- obtained from Tables 22 to 24 as for cables run horizontally; and

- if a  barrier is not provided at intervals of 3.5 m  or less to prevent the vertical flow    of air along the cable, determined in accordance with Clause 3.5.3 using the highest ambient air temperature up the cable   run.

      - Cables buried direct in the ground Where a  single-core or  multicore cable is buried directly in the ground and is separated by not less than 2  m  from a  cable or cables   of another circuit carrying substantial currents, no derating factor need be applied. Where  the circuits are separated by less than 2 m, the  appropriate  derating  factor  shall  be obtained from Table 25 except for installation methods not covered in this Standard, for which alternative specifications are recommended in Clause   1.2.

NOTE: The derating factors have been determined from the hottest cable in  the  group  and  assume that all cables are of the same thermal grade of insulation.

COPYRIGHT

23	AS/NZS 3008.1.2:1998

      - Cables in wiring enclosures    For cables in enclosures the following shall    apply:

- Underground wiring enclosures   Where a  single-core or multicore cable is installed  in an underground wiring enclosure and is separated by  not less than 2  m  from a  cable or cables of another enclosed circuit carrying substantial currents, no derating factor need be  applied. Where the enclosed circuits are separated by  less than 2  m, the appropriate derating factor shall be as given in Table 26 or, for installation  methods not covered in this Standard, alternative specifications as recommended in Clause 1.2.

- Other enclosures  Where cables are installed in an enclosure such as a switchboard,  the current-carrying capacity shall be determined from the unenclosed in air  conditions in Tables 3 to 8 with due regard being given to the derating factors when circuits are bunched.

NOTE: The selection of the derating factor should be based on the number of circuits that would be loaded; for example, where nine circuits are bunched but only six are loaded at     any one time, a derating factor of 0.57 from Table 22 would be applicable.

      - Conductors connected in parallel or passing more than once within a group or enclosure    In applying the derating factors of Tables 22 to 26    where—

- a group of conductors forming a circuit passes more than once through the same wiring enclosure, group of cables or group of enclosures;    or

- groups of conductors are connected in   parallel;

each separate group of conductors shall be regarded as a separate circuit.

In parallel circuits of single core cables, electrically asymmetric arrangements give rise to unequal load sharing and consequently the heating effects in some cables can be substantially greater than in a single   circuit.

NOTE: See Appendix B for recommended circuit configurations for  the  installation  of  single-core cables in  parallel.

    - Effect of ambient temperature The  current-carrying  capacities  given  in the tables of this Standard are based on a consistent ambient air temperature of 30°C and an ambient soil temperature of 15°C. Where other ambient  temperatures  apply,  the  appropriate rating factors shall be as given in Table    27.

NOTES:

      - In Australia the conditions of installation specify an ambient temperature of 40°C and a soil temperature of 25°C. A complete set of current rating tables, calculated for Australian conditions is given in AS/NZS  3008.1.1.

      - Particular consideration should be given to the existence of higher ambient air temperatures   in confined roof spaces, boiler rooms, cable tunnels, vertical shafts and the like. Similarly, lower ambient temperatures may apply for cables installed in concrete slabs on or above the surface of the  ground.

      - In practice the ambient air temperature may be measured by one of the following simple methods:

        - Before installation of cables   Measurement may be made by temperature sensors placed  in free air as close as practicable to the position at which the cables are to be installed.

        - After installation of cables    Measurement may be made by temperature sensors placed    in free air in the vicinity of the cables in such a  position  that  readings  are  not  influenced by heat arising from the cables. Where the measurements are made while the cables are loaded, e.g. as may be required by Clause 3.5.2.4 for vertical cable runs, the sensors should be placed approximately 500 mm, or 10 times the overall diameter of the cable, from the cables in a horizontal plane, or 150 mm below the cables.

If at the cable position, the ambient temperature, including any increase of temperature due to heat arising from equipment to which the cables are connected, does not exceed 30°C except for infrequent combinations of weather and load currents, then the current-carrying capacities given in the tables apply without    correction.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	24

    - Effect of depth of laying   The current-carrying capacities given in the tables of   this Standard are based on a depth of laying of 0.5 m as specified in Clauses 3.4.4 and

3.4.5. Where other depths of laying apply, the appropriate rating factors shall be  as  given  in Table 28.

NOTE: The rating factors are based  on  the assumption that  the effective thermal resistivity of  the ground is constant from a  depth of 0.5 m  to 3  m. Above and below these respective limits it   is considered that a reduction in effective thermal resistivity occurs due to the composition and moisture content of the  soil.

    - Effect of thermal resistivity of soil The current-carrying capacities given in the tables of this Standard are based on a soil thermal resistivity of 1.2°C.m/W.

Soil thermal resistivity varies greatly with soil composition, moisture retention qualities   and seasonal weather patterns as well as the variation in load carried by the cable. Higher current-carrying capacities are obtained in clay or peat soils which may have resistivities     as low as 0.8°C.m/W. Similarly, values as high as 2.5°C.m/W may be associated with well drained sands for  constantly loaded cables. The value of  1.2°C.m/W has been selected as  an average figure on the basis of soil types and assumes maximum thermal resistivity at  times of maximum  load.

If possible the actual value should be  measured along the  cable route as  it  can greatly affect the current-carrying capacity of the cable. Where values for  soil resistivities other than 1.2°C.m/W apply, the appropriate rating factors may be obtained from Table 29.

NOTE: Where the soil is known to be of poor quality and has a thermal resistivity greater than 1.2°C.m/W throughout much of the year, consideration should be given to the use of a  selected    or stabilized backfill material around the cables or wiring    enclosures.

Such backfill should completely surround the cable with a minimum thickness of 200 mm and could be used in lieu of the bedding required in NZS 3000.

The following two types of  material have a  worst-case or  dried-out thermal resistivity in  the order of 1.2°C.m/W:

- Cement-bound sand	A mixture of sand bound with cement in the ratio of 14:1 by volume, with water added to enable adequate compaction to be    achieved.

- Gravel/sand	A  mixture  of  a  selected  sand  having  a  dried-out  thermal  resistivity  of  not greater than 2.7°C.m/W, with an equal quantity of 10 mm coarse aggregate.

    - Effect of varying loads  The  current-carrying  capacities  given  in  the  tables  of this Standard and the derating factors given in Clauses 3.5.2 to 3.5.5 are based  on  continuous loading on all conductors. Where it can be shown that intermittent load  variations will occur or that all conductors cannot be loaded simultaneously, appropriate uprating factors may be  applied.

In many installations, groups of  cables comprise a  mixture of  loaded and  unloaded cables at any one time and the designer may justify the use of alternative derating factors to       those specified in Tables 22 to 26, if the connected loads have a known diversity. If the diversity is unknown or unobtainable by experiment, the design may have to be based on worst-case analysis of the possible load combinations at any one time. Some information    on the diversity of certain loads may be obtained from the determination of maximum demand in NZS  3000.

    - Effect of thermal insulation    Current-carrying capacities are given in Tables    3  to

14 of this Standard for unenclosed or enclosed cables surrounded by bulk  thermal  insulating materials which affect the rate of heat dissipation from the cables.

The rate of heat dissipation varies with the type and thickness of material used; a  comparative measure of the performance of different materials is known as the R-factor.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

25	AS/NZS 3008.1.2:1998

The current-carrying capacity values in the tables are based upon typical installation conditions and a range of different materials as described in Clause 3.4.3. Where different materials or installation conditions are used such that the rate of heat  dissipation  is adversely or favourably affected, lower or higher current-carrying capacities may be obtained respectively.

NOTES:

- Where a  length of cable not exceeding 150 mm passes through bulk thermal insulation, e.g.  for the connection of  a  lighting point, the cable need not be  considered as being surrounded by thermal insulation.

- A cable is considered to be affected by thermal insulation  if it is embedded  in,  or  surrounded by, insulating material. Cables lying on top of suitably rigid material do not in general come into this  consideration.

    - Effect of direct sunlight Current-carrying capacities are given  in  Tables 15,  20  and 21 for flexible cables and aerial cables exposed to direct sunlight. For other types of cable installed in locations exposed to direct solar radiation it will be necessary to make some provision for the effects of  the increased heating. This may be achieved by one of    the following means:

- Provision of a shield, screen or enclosure which allows for the natural ventilation of the cable.

- Reduction of the current-carrying capacity of the cable by an appropriate amount in accordance with the higher air temperature. As a rule-of-thumb alternative to any recommendation from a cable  manufacturer,  a  correction  factor  obtained  from  Table 27(1) for a temperature 20°C higher than the ambient air temperature may be applied.

NOTE: For further information on the effects of ultraviolet radiation it is recommended that the cable manufacturer be  consulted.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	26

| Method of installation | Horizontal spacings |  |  |  | Vertical spacings |
| --- | --- | --- | --- | --- | --- |
| Cables suspended from a |  |  |  |  |  |
| catenary wire where air |  |  |  |  |  |
| circulation is unrestricted |  |  |  |  |  |
| or spaced from surfaces |  |  |  |  |  |
| and supported on ladders, |  |  |  |  |  |
| racks, hangers or cleats |  |  |  |  |  |
| where the impedance of |  |  |  |  |  |
| the air flow around the |  |  |  |  |  |
| cable is not greater than |  |  |  |  |  |
| 10% |  |  |  |  |  |
| Cables spaced from surfaces and supported on perforated or unperforated cable trays where air circulation is partially restricted |  |  |  |  |  |
| Cables fixed directly to a wall, floor, ceiling or similar surface where air circulation is restricted |  |  |  |  |  |

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Single-core cables

| Method of installation | Horizontal spacings | Vertical spacings |
| --- | --- | --- |
| Cables suspended from a catenary wire where air circulation is unrestricted or spaced from surfaces and supported on ladders, racks, hangers or cleats where the impedance of the air flow around the cable is not greater than 10% |  |  |
| Cables spaced from surfaces and supported on perforated or unperforated cable trays where air circulation is partially restricted |  |  |
| Cables fixed directly to a wall, floor, ceiling or similar surface where air circulation is restricted |  |  |

  - Multicore cables

FIGURE  1	MINIMUM CABLE SPACINGS IN AIR TO AVOID  DERATING

COPYRIGHT

27	AS/NZS 3008.1.2:1998

NOTES TO FIGURE  1:

- D equals cable outside diameter or, in the case of a  flat multicore cable, the  maximum dimension of  the  cable.

- For  simplicity, the  illustrations depict balanced multiphase circuits. Where a  neutral conductor is  required    to be substantially loaded it shall be placed adjacent to the associated active conductors and the clearance measured as appropriate (see Note 3 for lightly loaded or unloaded conductors).

- The illustrations are intended to depict clearances required between cables operating at  or  near  their  sustained current-carrying capacity. Where the loading of any cable is less than  35%  of  such  sustained capacity it may be disregarded from the cable arrangements as its contribution to the mutual heating of the  group will be small. Such cables, which would include earthing conductors, lightly loaded neutrals and unloaded control wiring, may be placed adjacent to, or between, groups of associated loaded conductors.

- Where the cables concerned are not of the same size, the spacing  will  be  based  on  the  largest  cable  diameter in the adjacent  groups.

- The spacings are essentially minimum requirements to  avoid derating and  care should be  taken, particularly with smaller spacings, to avoid installation methods which would reduce these clearances. No restriction is placed on the number of circuits that may be arranged horizontally with the spacings given; however, care should be  taken if  more than three circuits are arranged vertically and full cable utilization       is required.

- Where the spacings are not achieved, smaller spacings and derating factors are laid down in the following tables:

  - For circuits installed directly on walls, floors or ceilings   . . . . . . . . . . . . . . . . . . . . . . . .  Table 22.

  - For circuits installed on trays, ladder supports, racks, hangers or cleats   . . . . . . . .  Tables 23 and    24.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Proportionally smaller spacings would be  acceptable where the cables in  the group are not loaded to  the      full current-carrying capacity. In such cases appropriate rating factors may be obtained from ERA Report 69-30.

COPYRIGHT

AS/NZS 3008.1.2:1998	28

### TABLE	2(1)

SCHEDULE OF INSTALLATION METHODS FOR CABLES DEEMED TO HAVE THE SAME CURRENT-CARRYING CAPACITY AND  CROSS-REFERENCES

TO APPLICABLE DERATING TABLES— UNENCLOSED IN  AIR

1	2	3	4	5	6

Item No.

Cable details (see Note 2)

Reference drawing (see Note 3)

Current-carrying capacity table reference

Methods of installation for cables deemed to have the same current-carrying  capacity (See Notes 4, 5 &  6)

Cables with minimum cable separations in air as shown for horizontal and   vertical

Derating table for more than one circuit

1	Two single- core cables

Tables 3 and  4

Columns 2 and  3

mounting and installed —

- spaced from a wall or vertical   surface;

- supported on  ladders, racks, perforated

trays, cleats or hangers;	23

or

2

Three single- core cables

3

4	Two single- core cables

5

Three single- core cables

6

- Two single-

core cables

- Three single- core cables

Tables 6 and  7

Columns 2 and  3

Tables 3 and  4

(see Note 5)

Columns 4 and  5

Tables 6 and  7

(see Note 5)

Columns 4 and  5

Tables 3 and  4

(see Note 4)

Columns 6 and  7

Tables 6 and  7

(see Note 4)

Columns 6 and  7

- suspended from a  catenary wire.	22

Cables with minimum cable spacings in air as  shown and installed —

- spaced from a wall or vertical   surface;

- supported on ladders, racks, perforated  or  unperforated trays, cleats or  hangers;

- in a switchboard or  similar enclosure;	23

or

- suspended from a  catenary wire.	22

Cables of the one circuit touching and installed —

- clipped direct to a wall, floor, ceiling or  similar surface;

- in a ventilated trench or   open trunking;	22

- buried directly in a plaster or render on   a wall; or

- in a switchboard or similar   enclosure.

- Two-core cables

Tables 9 and  10

(see Note 5)

Columns 2 and  3

Cables with minimum spacings in air as shown and installed —

- spaced from a wall or vertical   surface;

- supported on ladders, racks, perforated  or  unperforated trays, cleats or  hangers;

- in a switchboard or  similar enclosure;	24

or

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Three-core cables

11

Tables 12 and  13

(see Note 5)

Columns 2 and  3

- suspended from a catenary or as a self- supported overhead cable.

22

(continued)

COPYRIGHT

29	AS/NZS 3008.1.2:1998

TABLE	2(1)	(continued)

| 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- |
| Item No. | Cable details (see Note 2) | Reference drawing (see Note 3) | Current-carrying capacity table reference | Methods of installation for cables deemed to have the same current-carrying capacity (See Notes 4, 5 & 6) | Derating table for more than one circuit |
| 12 | Two-core cables |  | Tables 9 and 10 (see Note 4) Columns 4 and 5 | Cables installed — - clipped direct to a wall, floor, ceiling or similar surface; - buried directly in concrete or masonry above the ground or in plaster or render on a wall; - in a ventilated trench or open trunking; or - in a switchboard or similar enclosure | 22 |
| 13 | Three-core cables |  | Tables 12 and 13 (see Note 4) Columns 4 and 5 |  |  |

NOTES:

  - D equals cable outside diameter or, in the case of a flat multicore cable, the maximum dimension of the cable.

  - Earthing conductors, lightly loaded neutral conductors of  three-phase circuits and  conductors subject only to momentary loading, such as control wiring, shall not be counted in the number of cable cores.

  - See column headings of Tables 3 to    14.

  - See Table 22 for the derating factor applicable to a single  circuit  fixed  to  the  underside  of  a  ceiling  or  similar  horizontal surface.

  - See Tables 23 and 24 for the derating factors applicable to a single circuit fixed to perforated or unperforated trays.

  - See NZS 3000 for the restricted installation conditions of certain types of  cable, e.g. unarmoured cables in  plaster or  cement render on  walls.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	30

### TABLE  2(2)

SCHEDULE OF INSTALLATION METHODS FOR CABLES DEEMED TO HAVE THE SAME CURRENT-CARRYING CAPACITY AND CROSS-REFERENCES   TO

APPLICABLE DERATING TABLES— ENCLOSED

| 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- |
| Item No. | Cable details (see Note 1) | Reference drawing (see Note 2) | Current-carrying capacity table reference | Methods of installation for cables deemed to have the same current- carrying capacity (See Note 3) | Derating table for more than one circuit |
| 1 | Two single- core cables |  | Tables 3 and 4 Columns 8 and 9 | Cables in wiring enclosures installed in — - air; - plaster, cement render, masonry or concrete in a wall or floor; - a concrete slab on or above the surface of the ground; or - a ventilated trench. Cables installed in — - a wiring enclosure on a wall; or - an enclosed trench with a removable cover. | 22 |
| 2 | Three single- core cables |  | Tables 6 and 7 Columns 8 and 9 |  |  |
| 3 | Two single- core cables |  | Tables 3 and 4 Columns 10 and 11 | Cables enclosed or unenclosed — - partially surrounded by thermal insulation material; or - in an enclosed trench. | 22 |
| 4 | Three single- core cables |  | Tables 6 and 7 Columns 10 and 11 |  |  |
| 5 | Two single- core cables |  | Tables 3 and 4 Columns 12 and 13 | Unenclosed cables completely surrounded by thermal insulation | 22 |
| 6 | Three single- core cables |  | Tables 6 and 7 Columns 12 and 13 |  |  |
| 7 | Two-core cables |  | Table 9 Columns 6 to 9 Table 10 Columns 6 and 7 | Cables in wiring enclosures installed in — - air; - plaster, cement render, masonry or concrete in a wall or floor; - a concrete slab on or above the surface of the ground; or - a ventilated trench. Cables installed in — - closed trunking, or wiring enclosures on a wall; or - an enclosed trench with a removable cover. | 22 |
| 8 | Three-core cables |  | Table 12 Columns 6 to 9 Table 13 Columns 6 and 7 |  |  |
| 9 | Two-core cables | Table 9 Enclosed or unenclosed cables partially Columns 10 and 11 surrounded by thermal insulation. Table 10 Columns 8 and 9 22 |  |  |  |

10	Three-core cables

11	Two-core cables

Three-core cables

Table 12

Columns 10 and  11

Table 13

Columns 8 and  9

Table 9

Columns 12 and  13

Table 10

Columns 10 and  11

Table 12

Columns 12 and  13

Table 13

Columns 10 and  11

Enclosed or unenclosed cables completely surrounded by thermal insulation

22

12

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

31	AS/NZS 3008.1.2:1998

NOTES TO TABLE  2(2):

- Earthing conductors, lightly loaded neutral conductors of  three-phase circuits and  conductors subject only to momentary loading, such as control wiring, shall not be counted in the number of cable cores.

- See column headings of Tables 3 to    14.

- See NZS 3000 for the restricted installation conditions of certain types  of  cables,  e.g.  insulated  or  insulated  and  sheathed cables in  metallic and non-metallic  conduits.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	32

### TABLE  2(3)

SCHEDULE OF INSTALLATION METHODS FOR CABLES DEEMED TO HAVE    THE

SAME CURRENT-CARRYING CAPACITY AND CROSS-REFERENCES TO APPLICABLE DERATING TABLES— BURIED DIRECT IN THE  GROUND

| 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- |
| Item No. | Cable details (see Note 1) | Reference drawing (see Note 2) | Current-carrying capacity table reference | Methods of installation for cables deemed to have the same current- carrying capacity (see Note 3) | Derating table for more than one circuit |
| 1 | Two single- core cables |  | Tables 3 and 4 Columns 14 and 15 | Cables with a minimum depth of laying of — - 0.3 m under continuous concrete paved areas; or - 0.5 m in other locations. | 25(1) |
| 2 | Three single-core cables |  | Tables 6 and 7 Columns 14 and 15 |  |  |
| 3 | Two-core cables |  | Table 9 Columns 14 and 15 Table 10 Columns 12 and 13 |  | 25(2) |
| 4 | Three-core cables |  | Table 12 Columns 14 and 15 Table 13 Columns 12 and 13 |  |  |

NOTES:

- Earthing conductors, lightly loaded neutral conductors of  three-phase circuits and  conductors subject only to momentary loading, such as control wiring, shall not be counted in the number of cable cores.

- See column headings of Tables 3 to    14.

- See Tables 27 and 28 for rating factors applicable to different ambient soil temperatures and depths of laying.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

33	AS/NZS 3008.1.2:1998

### TABLE  2(4)

SCHEDULE OF INSTALLATION METHODS FOR CABLES DEEMED TO HAVE    THE

SAME CURRENT-CARRYING CAPACITY AND CROSS-REFERENCES TO APPLICABLE DERATING TABLES— ENCLOSED IN UNDERGROUND PIPES AND  DUCTS

| 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- |
| Item No. | Cable details (see Note 1) | Reference drawing (see Note 2) | Current-carrying capacity table reference | Methods of installation for cables deemed to have the same current- carrying capacity (see Note 3) | Derating table for more than one circuit |
| 1 | Two single- core cables |  | Tables 3 and 4 Columns 16 and 17 | Cables in a single enclosure laid — - directly under continuous concrete paved areas; or - minimum 0.5 m in other locations. | 26(2) |
| 2 | Three single-core cables |  | Tables 6 and 7 Columns 16 and 17 |  |  |
| 3 | One two- core cable |  | Table 9 Columns 16 and 17 Table 10 Columns 14 and 15 |  |  |
| 4 | One three- core cable |  | Table 12 Columns 16 and 17 Table 13 Columns 14 and 16 |  |  |
| 5 | Single-core cables |  | Tables 3 and 4 Columns 18 and 19 | Two enclosures laid — - directly under continuous concrete paved areas; or - minimum 0.5 m in other locations. | 26(1) |
| 6 |  |  | Tables 6 and 7 Columns 18 and 19 | Three enclosures laid — - directly under continuous concrete paved areas; or - minimum 0.5 m in other locations. |  |

NOTES:

- Earthing conductors, lightly loaded neutral conductors of three-phase circuits and conductors subject only to momentary loading, such as control wiring, shall not be counted in the number of cable cores.

- See column headings of Tables 3 to    14.

- See Tables 27 and 28 for rating factors applicable to different ambient soil temperatures and depths of laying.

COPYRIGHT

AS/NZS 3008.1.2:1998	34

### TABLE	3

CURRENT-CARRYING CAPACITIES OF TWO SINGLE-CORE 0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED CABLES  WITH

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

V-75, V-90,V-90HT, HFI-75-TP OR HFI-90-TP INSULATION (See Note    1)

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Unenclosed |  |  |  |  |  | Enclosed |  |  |  |  |  | Buried direct |  | Underground non-metallic wiring enclosure |  |  |  |
|  | Spaced |  | Spaced from |  | Touching |  | Non-metallic |  | In |  | Completely |  |  |  |  |  |  |  |
|  |  |  | surface |  |  |  | wiring |  | non-metallic |  | surrounded |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | enclosure in |  | wiring |  | by thermal |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | air |  | enclosure or |  | insulation |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | unenclosed |  |  |  |  |  |  |  |  |  |
| Con- ductor size |  |  |  |  |  |  |  |  | partially surrounded by thermal insulation |  |  |  |  |  |  |  |  |  |
| mm2 | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 1 | 18 | — | 18 | — | 15 | — | 15 | 11 | 11 | 9 | 7 | — | 26 | — | 20 | — | 23 | — |
| 1.5 | 24 | — | 24 | — | 18 | — | 18 | 14 | 15 | 11 | 9 | — | 34 | — | 26 | — | 30 | — |
| 2.5 | 34 | — | 33 | — | 26 | — | 25 | 19 | 21 | 16 | 14 | — | 47 | — | 36 | — | 41 | — |
| 4 | 46 | — | 44 | — | 35 | — | 34 | 26 | 27 | 22 | 18 | — | 62 | — | 46 | — | 53 | — |
| 6 | 58 | — | 56 | — | 46 | — | 43 | 34 | 35 | 29 | 23 | — | 78 | — | 58 | — | 66 | — |
| 10 | 79 | — | 76 | — | 62 | — | 60 | 47 | 48 | 39 | 31 | — | 103 | — | 78 | — | 87 | — |
| 16 | 105 | 81 | 101 | 78 | 82 | 63 | 81 | 63 | 65 | 51 | 41 | 32 | 132 | 105 | 100 | 77 | 110 | 86 |
| 25 | 143 | 109 | 137 | 105 | 111 | 86 | 111 | 86 | 90 | 71 | 55 | 42 | 176 | 138 | 132 | 101 | 149 |  |
| 35 | 177 | 137 | 165 | 131 | 137 | 106 | 131 | 103 | 105 | 82 | 67 | 52 | 209 | 160 | 160 | 121 | 176 | 110 |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 138 |
| 50 | 211 | 165 | 200 | 160 | 165 | 131 | 160 | 125 | 125 | 99 | — | — | 248 | 193 | 187 | 149 | 209 | 160 |
| 70 | 274 | 211 | 257 | 200 | 211 | 165 | 200 | 160 | 160 | 125 | — | — | 303 | 237 | 231 | 182 | 259 | 198 |
| 95 | 336 | 262 | 314 | 245 | 262 | 205 | 239 | 188 | 188 | 148 | — | — | 363 | 281 | 286 | 220 | 314 | 242 |
| 120 | 393 | 308 | 365 | 285 | 302 | 239 | 285 | 222 | 222 | 177 | — | — | 418 | 325 | 325 | 253 | 352 | 275 |
| 150 | 450 | 348 | 416 | 325 | 353 | 274 | 319 | 257 | 257 | 200 | — | — | 468 | 363 | 369 | 286 | 396 | 314 |
| 185 | 524 | 405 | 485 | 376 | 410 | 319 | 371 | 291 | 291 | 228 | — | — | 528 | 413 | 418 | 330 | 457 | 358 |
| 240 | 627 | 485 | 581 | 450 | 490 | 382 | 439 | 348 | 342 | 268 | — | — | 616 | 479 | 495 | 385 | 528 | 418 |
| 300 | 730 | 564 | 661 | 519 | 564 | 439 | — | — | — | — | — | — | 693 | 539 | 561 | 440 | 616 | 473 |
| 400 | 844 | 661 | 775 | 604 | 661 | 519 | — | — | — | — | — | — | 781 | 616 | 649 | 512 | 693 | 550 |
| 500 | 992 | 775 | 889 | 707 | 764 | 604 | — | — | — | — | — | — | 880 | 704 | 737 | 583 | 803 | 627 |
| 630 | 1151 | 912 | 1026 | 832 | 878 | 718 | — | — | — | — | — | — | 990 | 814 | 847 | 682 | 913 | 726 |

NOTES:

- Refer to Note 2 of Table 1 for information regarding the use of V-90 and V-90HT insulated cables.

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for cable configurations deemed to have the same current-carrying capacities as those illustrated.

- Derating factors may apply as   follows:

  - The current-carrying capacities apply to  single circuits; for grouped cable circuits see Clause 3.5.2 and Tables 22, 23, 25     and 26  for appropriate derating  factors.

  - For a  single circuit fixed to  the underside of  a  ceiling or  similar horizontal surface, see  Table 22  for  the derating factor    to  be  applied to  the current-carrying capacities given in  Columns 6  and 7.

  - For  a  single circuit fixed to  perforated or  unperforated cable tray, see  Table 23  for  the  derating factor to  be  applied to   the current-carrying capacities given in  Columns 4  and  5.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To calculate the single-phase voltage drop of  these configurations, multiply the  appropriate three-phase voltage drop value in  Table 40 or Table 43 by   1.155.

- These ratings are based on 30°C  ambient  air  temperature  and  15°C  ambient  soil  temperature.  For  other  conditions,  see  Clause 3.5.3.

COPYRIGHT

35	AS/NZS 3008.1.2:1998

### TABLE	4

CURRENT-CARRYING CAPACITIES OF TWO SINGLE-CORE 0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED CABLES  WITH

X-90, X-HF-90, R-EP-90, R-CPE-90, R-HF-90 OR R-CSP-90   INSULATION

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Unenclosed |  |  |  |  |  | Enclosed |  |  |  |  |  | Buried direct |  | Underground non-metallic wiring enclosure |  |  |  |
|  | Spaced |  | Spaced from |  | Touching |  | Non-metallic |  | In non- |  | Completely |  |  |  |  |  |  |  |
|  |  |  | surface |  |  |  | wiring |  | metallic |  | surround- |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | enclosure in |  | wiring |  | ed by |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | air |  | enclosure or |  | thermal |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | unenclosed |  | insulation |  |  |  |  |  |  |  |
| Con- ductor size |  |  |  |  |  |  |  |  | partially surrounded by thermal insulation |  |  |  |  |  |  |  |  |  |
| mm2 | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 1 | 22 | — | 22 | — | 18 | — | 18 | 13 | 15 | 12 | 9 | — | 30 | — | 22 | — | 26 | — |
| 1.5 | 29 | — | 28 | — | 22 | — | 22 | 18 | 19 | 14 | 11 | — | 39 | — | 29 | — | 33 | — |
| 2.5 | 40 | — | 40 | — | 31 | — | 31 | 24 | 26 | 21 | 15 | — | 54 | — | 40 | — | 45 | — |
| 4 | 53 | — | 52 | — | 41 | — | 41 | 33 | 35 | 28 | 21 | — | 68 | — | 51 | — | 59 | — |
| 6 | 67 | — | 66 | — | 52 | — | 52 | 43 | 44 | 35 | 26 | — | 86 | — | 64 | — | 73 | — |
| 10 | 92 | — | 90 | — | 72 | — | 72 | 59 | 62 | 48 | 35 | — | 112 | — | 86 | — | 96 | — |
| 16 | 121 | 96 | 121 | 92 | 95 | 74 | 95 | 74 | 81 | 64 | 47 | 36 | 150 | 112 | 112 | 86 | 123 | 95 |
| 25 | 165 | 127 | 160 | 121 | 127 | 100 | 127 | 100 | 110 | 89 | 64 | 50 | 193 | 150 | 144 | 112 | 161 | 123 |
| 35 | 204 | 160 | 193 | 149 | 160 | 121 | 160 | 121 | 132 | 103 | 79 | 62 | 230 | 177 | 171 | 134 | 193 | 150 |
| 50 | 253 | 193 | 237 | 182 | 193 | 149 | 193 | 149 | 160 | 127 | — | — | 273 | 214 | 209 | 161 | 230 | 177 |
| 70 | 319 | 248 | 303 | 231 | 248 | 193 | 242 | 193 | 198 | 154 | — | — | 337 | 262 | 257 | 198 | 284 | 219 |
| 95 | 396 | 308 | 374 | 286 | 308 | 237 | 286 | 237 | 237 | 187 | — | — | 401 | 310 | 310 | 241 | 337 | 262 |
| 120 | 462 | 363 | 435 | 336 | 358 | 281 | 341 | 281 | 281 | 220 | — | — | 455 | 353 | 358 | 278 | 391 | 305 |
| 150 | 534 | 413 | 495 | 385 | 413 | 319 | 385 | 319 | 314 | 253 | — | — | 514 | 396 | 401 | 310 | 439 | 342 |
| 185 | 627 | 484 | 572 | 446 | 479 | 374 | 440 | 374 | 363 | 286 | — | — | 578 | 455 | 465 | 358 | 503 | 391 |
| 240 | 748 | 583 | 682 | 534 | 572 | 451 | 523 | 440 | 429 | 341 | — | — | 674 | 524 | 546 | 428 | 589 | 455 |
| 300 | 869 | 671 | 792 | 616 | 671 | 523 | — | — | — | — | — | — | 760 | 599 | 621 | 482 | 674 | 524 |
| 400 | 1012 | 792 | 924 | 726 | 781 | 616 | — | — | — | — | — | — | 867 | 685 | 717 | 567 | 770 | 599 |
| 500 | 1188 | 935 | 1067 | 847 | 902 | 726 | — | — | — | — | — | — | 974 | 781 | 813 | 653 | 877 | 696 |
| 630 | 1386 | 1100 | 1221 | 990 | 1045 | 847 | — | — | — | — | — | — | 1102 | 888 | 952 | 770 | 1017 | 803 |

NOTES:

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for  cable  configurations  deemed  to  have  the  same  current-carrying  capacities as  those illustrated.

- Derating factors may apply as   follows:

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

The current-carrying capacities  apply  to  single  circuits;  for  grouped  cable  circuits  see  Clause  3.5.2  and  Tables 22, 23, 25 and 26 for appropriate derating factors.

  - For a single circuit fixed to the underside of a  ceiling  or  similar  horizontal  surface,  see  Table  22  for  the  derating factor to  be  applied to  the current-carrying capacities given in  Columns 6  and  7.

  - For a single circuit fixed to  perforated or  unperforated cable tray, see  Table 23  for the  derating factor to  be  applied to  the current-carrying capacities given in  Columns 4  and  5.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To calculate the single-phase voltage drop of  these configurations, multiply the appropriate three-phase voltage drop  value in Table 40 or Table 43 by    1.155.

- These ratings are based on  30°C ambient air temperature and 15°C ambient soil temperature. For other conditions,         see Clause 3.5.3.

COPYRIGHT

AS/NZS 3008.1.2:1998	36

### TABLE	5

CURRENT-CARRYING CAPACITIES OF TWO SINGLE-CORE 0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED CABLES  WITH

R-HF-110, R-E-110 OR X-HF-110  INSULATION

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |
|  | Unenclosed |  |  | Enclosed |  |  | Buried direct | Underground non-metallic wiring enclosure |  |
|  | Spaced | Spaced from | Touching | Metallic | In metallic | Completely |  |  |  |
|  |  | surface |  | wiring | wiring | surrounded |  |  |  |
|  |  |  |  | enclosure in | enclosure or | by thermal |  |  |  |
|  |  |  |  | air | unenclosed | insulation |  |  |  |
|  |  |  |  |  | partially |  |  |  |  |
| Con- ductor size |  |  |  |  | surrounded by thermal insulation |  |  |  |  |
| mm2 | Cu | Cu | Cu | Cu | Cu | Cu | Cu | Cu | Cu |
| 1 | 27 | 26 | 21 | 21 | 17 | 11 | 33 | 25 | 29 |
| 1.5 | 34 | 33 | 27 | 27 | 21 | 14 | 41 | 32 | 36 |
| 2.5 | 48 | 47 | 39 | 37 | 30 | 19 | 58 | 45 | 50 |
| 4 | 63 | 62 | 50 | 49 | 40 | 25 | 75 | 58 | 65 |
| 6 | 80 | 78 | 63 | 62 | 49 | 32 | 94 | 72 | 81 |
| 10 | 112 | 106 | 87 | 83 | 66 | 43 | 127 | 95 | 106 |
| 16 | 144 | 139 | 112 | 112 | 89 | 57 | 164 | 127 | 138 |
| 25 | 198 | 187 | 155 | 144 | 118 | 77 | 212 | 159 | 180 |
| 35 | 241 | 230 | 187 | 177 | 139 | 94 | 254 | 196 | 212 |
| 50 | 294 | 278 | 230 | 219 | 177 | — | 297 | 233 | 254 |
| 70 | 375 | 353 | 289 | 273 | 219 | — | 366 | 286 | 313 |
| 95 | 465 | 433 | 364 | 342 | 273 | — | 440 | 350 | 382 |
| 120 | 546 | 503 | 423 | 396 | 316 | — | 504 | 398 | 435 |
| 150 | 621 | 578 | 487 | 460 | 369 | — | 562 | 456 | 488 |
| 185 | 717 | 663 | 567 | 530 | 423 | — | 636 | 519 | 562 |
| 240 | 867 | 792 | 674 | 631 | 508 | — | 742 | 615 | 647 |
| 300 | 995 | 920 | 781 | — | — | — | 837 | 710 | 753 |
| 400 | 1166 | 1070 | 910 | — | — | — | 954 | 806 | 859 |
| 500 | 1370 | 1231 | 1059 | — | — | — | 1081 | 922 | 996 |
| 630 | 1605 | 1423 | 1231 | — | — | — | 1219 | 1071 | 1134 |

NOTES:

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for cable  configurations  deemed  to  have  the  same  current-carrying  capacities as  those illustrated.

- Derating factors may apply as   follows:

  - The current-carrying capacities  apply  to  single  circuits,  for  grouped  cable  circuits  see  Clause  3.5.2  and  Tables 22, 23, 25 and 26 for appropriate derating factors.

  - For a single circuit fixed to the underside of a ceiling  or  similar  horizontal  surface,  see  Table  22  for  the  derating factor to  be  applied to  the current-carrying capacities given in  Column  4.

  - For a  single circuit fixed to  perforated or  unperforated cable tray, see Table 23  for the derating factor to  be   applied to  the current-carrying capacities given in  Column  3.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To calculate the single-phase voltage drop of these configurations, multiply the appropriate three-phase voltage drop  value in Table 40 or Table 43 by    1.155.

- These ratings are  based on  30°C ambient air  temperature and  15°C ambient soil temperature. For  other conditions,    see Clause 3.5.3.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

37	AS/NZS 3008.1.2:1998

### TABLE	6

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

CURRENT-CARRYING CAPACITIES OF THREE SINGLE-CORE 0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED CABLES  WITH

V-75, V-90, V-90HT, HFI-75-TP OR HFI-90-TP INSULATION (See Note    1)

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Unenclosed |  |  |  |  |  | Enclosed |  |  |  |  |  | Buried direct |  | Underground non-metallic wiring enclosure |  |  |  |
|  | Spaced |  | Spaced from |  | Touching |  | Non-metallic |  | In |  | Completely |  |  |  |  |  |  |  |
|  |  |  | surface |  |  |  | wiring |  | non-metallic |  | surrounded |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | enclosure in |  | wiring |  | by thermal |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | air |  | enclosure or |  | insulation |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | unenclosed |  |  |  |  |  |  |  |  |  |
| Con- ductor size |  |  |  |  |  |  |  |  | partially surrounded by thermal insulation |  |  |  |  |  |  |  |  |  |
| mm2 | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 1 | 18 | — | 16 | — | 15 | — | 13 | 10 | 11 | 9 | 7 | — | 23 | — | 18 | — | 21 | — |
| 1.5 | 23 | — | 19 | — | 18 | — | 16 | 13 | 14 | 10 | 9 | — | 30 | — | 22 | — | 28 | — |
| 2.5 | 33 | — | 29 | — | 26 | — | 23 | 18 | 19 | 15 | 14 | — | 41 | — | 31 | — | 37 | — |
| 4 | 43 | — | 38 | — | 35 | — | 30 | 23 | 26 | 21 | 18 | — | 54 | — | 41 | — | 48 | — |
| 6 | 56 | — | 48 | — | 46 | — | 39 | 30 | 33 | 25 | 23 | — | 67 | — | 51 | — | 59 | — |
| 10 | 76 | — | 66 | — | 62 | — | 54 | 41 | 44 | 34 | 31 | — | 89 | — | 67 | — | 79 | — |
| 16 | 101 | 78 | 88 | 67 | 82 | 63 | 71 | 55 | 59 | 46 | 41 | 32 | 116 | 89 | 88 | 67 | 101 | 78 |
| 25 | 137 | 106 | 120 | 91 | 111 | 86 | 99 | 78 | 82 | 64 | 55 | 42 | 149 | 116 | 116 | 88 | 132 | 101 |
| 35 | 171 | 131 | 143 | 113 | 137 | 106 | 114 | 90 | 96 | 74 | 67 | 52 | 176 | 138 | 138 | 107 | 160 | 121 |
| 50 | 205 | 160 | 177 | 137 | 165 | 131 | 143 | 108 | 114 | 90 | — | — | 209 | 160 | 165 | 127 | 187 | 143 |
| 70 | 262 | 205 | 222 | 177 | 211 | 165 | 177 | 137 | 143 | 113 | — | — | 259 | 198 | 204 | 160 | 231 | 182 |
| 95 | 325 | 257 | 279 | 217 | 262 | 205 | 205 | 165 | 171 | 137 | — | — | 308 | 237 | 248 | 193 | 281 | 215 |
| 120 | 382 | 296 | 325 | 257 | 302 | 239 | 251 | 194 | 200 | 160 | — | — | 347 | 270 | 286 | 220 | 319 | 248 |
| 150 | 439 | 342 | 376 | 291 | 353 | 274 | 285 | 222 | 228 | 182 | — | — | 391 | 303 | 319 | 253 | 352 | 281 |
| 185 | 507 | 393 | 439 | 342 | 405 | 319 | 325 | 251 | 262 | 205 | — | — | 440 | 341 | 369 | 286 | 407 | 319 |
| 240 | 616 | 473 | 519 | 405 | 485 | 376 | 388 | 302 | 308 | 245 | — | — | 512 | 402 | 429 | 336 | 473 | 369 |
| 300 | 707 | 553 | 604 | 473 | 559 | 439 | 445 | 348 | 353 | 285 | — | — | 572 | 451 | 495 | 385 | 545 | 424 |
| 400 | 832 | 650 | 695 | 553 | 650 | 519 | 519 | 405 | 410 | 331 | — | — | 649 | 517 | 561 | 446 | 616 | 484 |
| 500 | 969 | 752 | 809 | 650 | 752 | 604 | 604 | 467 | 473 | 382 | — | — | 737 | 594 | 649 | 512 | 715 | 561 |
| 630 | 1129 | 901 | 935 | 764 | 866 | 718 | 707 | 547 | 553 | 445 | — | — | 825 | 682 | 726 | 594 | 803 | 638 |

NOTES:

- Refer to Note 2 of Table 1 for information regarding the use of V-90 and V-90HT insulated cables.

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for  cable  configurations  deemed  to  have  the  same  current-carrying  capacities as  those illustrated.

- Derating factors may apply as   follows:

  - The  current-carrying  capacities  apply  to  single  circuits;  for  grouped  cable  circuits  see  Clause  3.5.2  and  Tables 22, 23, 25 and 26 for appropriate derating factors.

  - For a single circuit fixed to the underside of  a  ceiling  or  similar  horizontal  surface,  see  Table  22  for  the  derating factor to  be  applied to  the current-carrying capacities given in  Columns 6  and  7.

  - For a single circuit fixed to perforated or unperforated cable tray,  see  Table  23  for  the  derating  factor  to  be applied to  the current-carrying capacities given in  Columns 4  and  5.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To calculate the single-phase voltage drop of  these configurations, multiply the appropriate three-phase voltage drop  value in Table 40 or Table 43 by    1.155.

- These ratings are based on  30°C ambient air temperature and 15°C ambient soil temperature. For other conditions,         see Clause 3.5.3.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	38

### TABLE	7

CURRENT-CARRYING CAPACITIES OF THREE SINGLE-CORE 0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED CABLES  WITH

X-90, X-HF-90, R-EP-90, R-CPE-90, R-HF-90 OR R-CSP-90   INSULATION

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Unenclosed non-metallic wiring enclosure |  |  |  |  |  | Enclosed |  |  |  |  |  | Buried direct |  | Underground non-metallic wiring enclosure |  |  |  |
|  | Spaced |  | Spaced from |  | Touching |  | Non-metallic |  | In |  | Completely |  |  |  |  |  |  |  |
|  |  |  | surface |  |  |  | wiring |  | non-metallic |  | surrounded |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | enclosure in |  | wiring |  | by thermal |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | air |  | enclosure or |  | insulation |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | unenclosed |  |  |  |  |  |  |  |  |  |
| Con- ductor size |  |  |  |  |  |  |  |  | partially surrounded by thermal insulation |  |  |  |  |  |  |  |  |  |
| mm2 | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 1 | 21 | — | 18 | — | 18 | — | 15 | 12 | 11 | 10 | 9 | — | 26 | — | 19 | — | 24 | — |
| 1.5 | 28 | — | 23 | — | 22 | — | 20 | 15 | 13 | 13 | 11 | — | 33 | — | 25 | — | 30 | — |
| 2.5 | 39 | — | 33 | — | 31 | — | 28 | 21 | 19 | 18 | 15 | — | 45 | — | 34 | — | 42 | — |
| 4 | 51 | — | 44 | — | 41 | — | 36 | 29 | 31 | 24 | 21 | — | 59 | — | 44 | — | 54 | — |
| 6 | 65 | — | 55 | — | 52 | — | 46 | 37 | 40 | 32 | 26 | — | 73 | — | 56 | — | 66 | — |
| 10 | 89 | — | 76 | — | 72 | — | 64 | 53 | 55 | 44 | 35 | — | 97 | — | 74 | — | 87 | — |
| 16 | 121 | 92 | 101 | 78 | 95 | 74 | 86 | 70 | 73 | 58 | 47 | 36 | 123 | 97 | 95 | 74 | 112 | 86 |
| 25 | 160 | 127 | 138 | 107 | 127 | 100 | 121 | 99 | 101 | 80 | 64 | 50 | 161 | 123 | 123 | 96 | 144 | 112 |
| 35 | 198 | 154 | 171 | 132 | 160 | 121 | 138 | 116 | 116 | 94 | 79 | 62 | 193 | 150 | 150 | 118 | 171 | 134 |
| 50 | 242 | 187 | 209 | 160 | 193 | 149 | 171 | 138 | 143 | 110 | — | — | 230 | 177 | 182 | 139 | 209 | 161 |
| 70 | 308 | 242 | 264 | 204 | 248 | 193 | 209 | 176 | 176 | 143 | — | — | 278 | 219 | 225 | 177 | 251 | 198 |
| 95 | 385 | 297 | 330 | 253 | 308 | 237 | 253 | 215 | 215 | 171 | — | — | 337 | 262 | 268 | 209 | 300 | 235 |
| 120 | 451 | 352 | 385 | 297 | 358 | 281 | 297 | 253 | 248 | 198 | — | — | 380 | 294 | 310 | 241 | 348 | 273 |
| 150 | 517 | 402 | 446 | 347 | 413 | 319 | 341 | 286 | 281 | 226 | — | — | 428 | 332 | 353 | 273 | 391 | 300 |
| 185 | 605 | 468 | 517 | 402 | 479 | 374 | 391 | 330 | 325 | 259 | — | — | 482 | 375 | 401 | 310 | 449 | 348 |
| 240 | 726 | 561 | 616 | 484 | 572 | 446 | 462 | 396 | 385 | 303 | — | — | 556 | 439 | 471 | 369 | 519 | 407 |
| 300 | 847 | 660 | 715 | 561 | 660 | 517 | 534 | 457 | 440 | 352 | — | — | 631 | 498 | 546 | 428 | 599 | 465 |
| 400 | 990 | 770 | 836 | 660 | 770 | 616 | 616 | 534 | 512 | 407 | — | — | 717 | 567 | 621 | 487 | 685 | 535 |
| 500 | 1155 | 913 | 957 | 770 | 891 | 715 | 715 | 616 | 594 | 468 | — | — | 803 | 642 | 717 | 578 | 770 | 610 |
| 630 | 1353 | 1078 | 1111 | 902 | 1034 | 847 | 836 | 726 | 693 | 550 | — | — | 899 | 738 | 813 | 663 | 888 | 706 |

NOTES:

- Refer to  Tables 2(1), 2(2), 2(3) and 2(4) for cable configurations deemed to  have the  same current-carrying capacities     as those illustrated.

- Derating factors may apply as   follows:

  - The  current-carrying  capacities  apply  to  single  circuits;  for  grouped  cable  circuits  see  Clause  3.5.2  and  Tables 22, 23, 25 and 26 for appropriate derating factors.

  - For a single circuit fixed to the underside of a ceiling or similar horizontal surface, see Table 22 for the derating  factor to  be  applied to  the current-carrying capacities given in  Columns 6  and 7.

  - For a single circuit fixed to perforated or unperforated cable tray,  see  Table  23  for  the  derating  factor  to  be applied to  the current-carrying capacities given in  Columns 4  and  5.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To determine  the  three-phase  voltage  drop  of  these  configurations,  refer  to  the  appropriate  value  in  Table  40,  Table 41, Table 43 or Table   44.

- These ratings are based on 30°C ambient air temperature and 15°C ambient soil temperature. For other conditions, see Clause 3.5.3.

COPYRIGHT

39	AS/NZS 3008.1.2:1998

### TABLE	8

CURRENT-CARRYING CAPACITIES OF THREE SINGLE-CORE 0.6/1 kV SHEATHED AND UNSHEATHED NON-ARMOURED CABLES  WITH

R-HF-110, R-E-110 OR X-HF-110  INSULATION

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |
|  | Unenclosed |  |  | Enclosed |  |  | Buried direct | Underground non- metallic wiring enclosure |  |
|  | Spaced | Spaced | Touching | Metallic | In metallic | Completely |  |  |  |
|  |  | from |  | wiring | wiring | surrounded |  |  |  |
|  |  | surface |  | enclosure | enclosure or | by thermal |  |  |  |
|  |  |  |  | in air | unenclosed | insulation |  |  |  |
|  |  |  |  |  | partially |  |  |  |  |
|  |  |  |  |  | surrounded by |  |  |  |  |
| Con- ductor |  |  |  |  | thermal insulation |  |  |  |  |
| size |  |  |  |  |  |  |  |  |  |
| mm2 | Cu | Cu | Cu | Cu | Cu | Cu | Cu | Cu | Cu |
| 1 | 26 | 22 | 21 | 18 | 15 | 11 | 29 | 22 | 27 |
| 1.5 | 33 | 29 | 27 | 24 | 19 | 14 | 36 | 28 | 33 |
| 2.5 | 46 | 41 | 39 | 34 | 27 | 19 | 50 | 39 | 46 |
| 4 | 61 | 54 | 50 | 44 | 35 | 25 | 65 | 50 | 58 |
| 6 | 78 | 67 | 63 | 55 | 44 | 32 | 81 | 63 | 73 |
| 10 | 106 | 92 | 87 | 76 | 61 | 43 | 106 | 84 | 95 |
| 16 | 139 | 123 | 112 | 100 | 79 | 57 | 138 | 106 | 127 |
| 25 | 187 | 166 | 155 | 134 | 107 | 77 | 180 | 143 | 159 |
| 35 | 235 | 203 | 187 | 161 | 128 | 94 | 212 | 170 | 191 |
| 50 | 284 | 246 | 230 | 193 | 155 | — | 249 | 201 | 228 |
| 70 | 364 | 310 | 289 | 251 | 198 | — | 307 | 249 | 281 |
| 95 | 449 | 391 | 364 | 305 | 246 | — | 371 | 302 | 339 |
| 120 | 524 | 449 | 423 | 358 | 289 | — | 419 | 350 | 387 |
| 150 | 610 | 519 | 487 | 407 | 326 | — | 472 | 392 | 429 |
| 185 | 706 | 599 | 567 | 482 | 385 | — | 530 | 456 | 498 |
| 240 | 845 | 717 | 674 | 589 | 471 | — | 615 | 541 | 572 |
| 300 | 974 | 835 | 781 | 674 | 535 | — | 700 | 615 | 668 |
| 400 | 1145 | 974 | 910 | 770 | 610 | — | 795 | 700 | 753 |
| 500 | 1338 | 1124 | 1049 | 920 | 738 | — | 890 | 816 | 880 |
| 630 | 1562 | 1305 | 1209 | 1049 | 845 | — | 1007 | 912 | 986 |

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

NOTES:

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for cable configurations deemed to  have  the  same  current-carrying  capacities  as  those  illustrated.

- Derating factors may apply as   follows:

  - The current-carrying capacities apply to  single circuits; for  grouped cable circuits see  Clause 3.5.2 and  Tables 22,  23,  25  and  26    for appropriate derating  factors.

  - For a single circuit fixed to the underside of a ceiling  or  similar  horizontal  surface,  see  Table  22  for  the  derating  factor  to  be applied to  the current-carrying capacities given in  Column  4.

  - For a single circuit fixed to perforated or unperforated cable tray, see Table 23 for the derating factor to be applied to the current-  carrying capacities given in  Column  3.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To  determine the  three-phase voltage drop of  these configurations, refer to  the  appropriate value in  Table 40,  Table 41,  Table 43  or  Table 44.

- These ratings are based on 30°C ambient air temperature and 15°C ambient soil temperature. For other conditions, see Clause 3.5.3.

COPYRIGHT

AS/NZS 3008.1.2:1998	40

### TABLE	9

CURRENT-CARRYING CAPACITIES OF TWO-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED) CABLES WITH   OR

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

WITHOUT EARTH CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH V-75, V-90, HFI-75-TP OR HFI-90-TP INSULATION (See Note    1)

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Unenclosed |  |  |  | Enclosed |  |  |  |  |  |  |  | Buried direct |  | Underground non-metallic wiring enclosure |  |
|  | Spaced |  | Touching |  | Non-metallic |  | Non-metallic |  | In non-metallic |  | Completely |  |  |  |  |  |
|  |  |  |  |  | wiring |  | wiring enclosure |  | wiring |  | surrounded by |  |  |  |  |  |
|  |  |  |  |  | enclosure in |  | in air — flat |  | enclosure or |  | thermal |  |  |  |  |  |
|  |  |  |  |  | air — round |  | cable |  | unenclosed |  | insulation |  |  |  |  |  |
|  |  |  |  |  | cable |  |  |  | partially |  |  |  |  |  |  |  |
| Con- ductor size |  |  |  |  |  |  |  |  | surrounded by thermal insulation |  |  |  |  |  |  |  |
| mm2 | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 1 | 17 | — | 16 | — | 13 | 10 | 15 | 11 | 11 | 9 | 8 | — | 24 | — | 19 | — |
| 1.5 | 22 | — | 21 | — | 16 | 13 | 19 | 15 | 15 | 11 | 10 | — | 31 | — | 24 | — |
| 2.5 | 31 | — | 30 | — | 23 | 17 | 25 | 19 | 21 | 16 | 15 | — | 44 | — | 34 | — |
| 4 | 42 | — | 39 | — | 30 | 23 | 33 | 25 | 27 | 22 | 19 | — | 57 | — | 44 | — |
| 6 | 52 | — | 50 | — | 39 | 30 | 42 | 32 | 35 | 27 | 25 | — | 72 | — | 56 | — |
| 10 | 73 | — | 68 | — | 54 | 41 | 57 | 43 | 49 | 38 | 34 | — | 96 | — | 75 | — |
| 16 | 97 | 75 | 91 | 71 | 72 | 55 | 75 | 57 | 65 | 50 | 46 | 35 | 127 | 97 | 97 | 75 |
| 25 | 131 | 100 | 120 | 95 | 100 | 76 | 101 | 76 | 90 | 71 | 60 | 47 | 160 | 127 | 127 | 98 |
| 35 | 160 | 125 | 148 | 114 | 120 | 89 | 120 | 89 | 105 | 82 | 74 | 58 | 198 | 154 | 154 | 121 |
| 50 | 194 | 148 | 182 | 143 | 143 | 107 | 143 | 107 | 125 | 99 | — | — | 231 | 182 | 182 | 143 |
| 70 | 245 | 188 | 228 | 177 | 177 | 137 | — | — | 160 | 125 | — | — | 286 | 220 | 226 | 176 |
| 95 | 302 | 234 | 285 | 217 | 217 | 165 | — | — | 188 | 148 | — | — | 341 | 264 | 275 | 215 |
| 120 | 348 | 274 | 331 | 257 | 257 | 194 | — | — | 222 | 177 | — | — | 391 | 303 | 319 | 248 |
| 150 | 399 | 308 | 376 | 291 | 291 | 217 | — | — | 251 | 200 | — | — | 440 | 341 | 358 | 275 |
| 185 | 462 | 359 | 428 | 336 | 336 | 251 | — | — | 291 | 228 | — | — | 495 | 385 | 407 | 319 |
| 240 | 542 | 428 | 507 | 399 | 393 | 296 | — | — | 342 | 274 | — | — | 572 | 446 | 473 | 369 |
| 300 | 627 | 490 | 581 | 456 | 456 | 342 | — | — | 393 | 314 | — | — | 649 | 506 | 545 | 429 |
| 400 | 718 | 570 | 673 | 530 | 530 | 399 | — | — | 462 | 365 | — | — | 726 | 583 | 616 | 490 |
| 500 | 821 | 661 | 764 | 616 | 707 | 564 | — | — | 564 | 450 | — | — | 814 | 660 | 715 | 572 |

NOTES:

- Refer to Note 2 of Table 1 for information regarding the use of V-90 insulated cables.

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for cable configurations deemed to have the same current-carrying capacities as those illustrated.

- Derating factors may apply as   follows:

  - The  current-carrying capacities apply to  single circuits; for  grouped cable circuits see  Clause 3.5.2 and  Tables 22,  23,  25   and 26  for appropriate derating  factors.

  - For a  single circuit fixed to  the underside of  a  ceiling or  similar horizontal surface, see Table 22  for the derating factor to      be  applied to  the current-carrying capacities given in  Columns 4  and  5.

  - For a single circuit fixed to unperforated cable tray, see Table 24  for  the  derating  factor  to  be  applied  to  the  current- carrying capacities given in Columns 2 and   3.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To calculate the single-phase voltage drop of these configurations, multiply the  appropriate  three-phase voltage drop value  in  Table 42 or Table 45 by   1.155.

- These ratings are based on  30°C  ambient  air  temperature  and  15°C  ambient  soil  temperature.  For  other  conditions,  see  Clause 3.5.3.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

41	AS/NZS 3008.1.2:1998

### TABLE	10

CURRENT-CARRYING CAPACITIES OF TWO-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED) CABLES WITH   OR

WITHOUT EARTH CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH X-90, X-HF-90, R-EP-90,  R-CPE-90,

R-HF-90 OR R-CSP-90  INSULATION

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Unenclosed |  |  |  | Enclosed |  |  |  |  |  | Buried direct |  | Underground non-metallic wiring enclosure |  |
|  | Spaced |  | Touching |  | Non-metallic |  | In non-metallic |  | Completely |  |  |  |  |  |
|  |  |  |  |  | wiring enclosure |  | wiring enclosure |  | surrounded by |  |  |  |  |  |
|  |  |  |  |  | in air |  | or unenclosed |  | thermal |  |  |  |  |  |
|  |  |  |  |  |  |  | partially |  | insulation |  |  |  |  |  |
|  |  |  |  |  |  |  | surrounded by |  |  |  |  |  |  |  |
| Con- |  |  |  |  |  |  | thermal |  |  |  |  |  |  |  |
| ductor |  |  |  |  |  |  | insulation |  |  |  |  |  |  |  |
| size |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| mm2 | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 1 | 20 | — | 19 | — | 14 | 11 | 15 | 12 | 10 | — | 28 | — | 21 | — |
| 1.5 | 26 | — | 24 | — | 19 | 14 | 19 | 15 | 12 | — | 35 | — | 27 | — |
| 2.5 | 37 | — | 34 | — | 26 | 20 | 26 | 20 | 18 | — | 49 | — | 37 | — |
| 4 | 50 | — | 46 | — | 36 | 26 | 35 | 28 | 23 | — | 64 | — | 49 | — |
| 6 | 63 | — | 58 | — | 46 | 35 | 45 | 35 | 30 | — | 80 | — | 61 | — |
| 10 | 86 | — | 80 | — | 65 | 48 | 62 | 48 | 40 | — | 107 | — | 82 | — |
| 16 | 116 | 89 | 107 | 83 | 87 | 66 | 81 | 64 | 54 | 42 | 139 | 107 | 107 | 83 |
| 25 | 154 | 121 | 143 | 110 | 121 | 92 | 116 | 89 | 73 | 56 | 182 | 139 | 139 | 107 |
| 35 | 193 | 149 | 176 | 138 | 143 | 109 | 132 | 103 | 89 | 69 | 219 | 171 | 171 | 128 |
| 50 | 231 | 182 | 215 | 171 | 176 | 132 | 160 | 127 | — | — | 262 | 203 | 203 | 155 |
| 70 | 297 | 231 | 275 | 215 | 220 | 171 | 198 | 154 | — | — | 321 | 251 | 251 | 193 |
| 95 | 363 | 281 | 341 | 264 | 264 | 204 | 237 | 187 | — | — | 385 | 300 | 305 | 235 |
| 120 | 424 | 330 | 396 | 308 | 314 | 242 | 281 | 220 | — | — | 439 | 342 | 348 | 273 |
| 150 | 484 | 374 | 451 | 352 | 358 | 275 | 314 | 253 | — | — | 492 | 380 | 401 | 310 |
| 185 | 561 | 435 | 523 | 407 | 413 | 319 | 363 | 292 | — | — | 556 | 433 | 455 | 353 |
| 240 | 660 | 517 | 616 | 484 | 490 | 385 | 429 | 341 | — | — | 642 | 503 | 535 | 417 |
| 300 | 759 | 594 | 704 | 561 | 572 | 446 | 495 | 391 | — | — | 728 | 567 | 610 | 482 |
| 400 | 880 | 704 | 825 | 649 | 660 | 523 | 572 | 457 | — | — | 824 | 653 | 696 | 556 |
| 500 | 1012 | 803 | 935 | 748 | 847 | 682 | 682 | 545 | — | — | 920 | 738 | 803 | 642 |

NOTES:

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for cable configurations deemed to have the same current-carrying capacities as those illustrated.

- Derating factors may apply as   follows:

  - The  current-carrying capacities apply to  single circuits; for  grouped cable circuits see  Clause 3.5.2 and  Tables 22,  24,  25   and 26  for appropriate derating  factors.

  - For a  single circuit fixed to  the underside of  a  ceiling or  similar horizontal surface, see Table 22  for the derating factor to      be  applied to  the current-carrying capacities given in  Columns 4  and  5.

  - For a single circuit fixed to unperforated cable tray, see Table 24  for  the  derating  factor  to  be  applied  to  the  current- carrying capacities given in Columns 2 and   3.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To calculate the single-phase voltage drop of these configurations, multiply  the  appropriate three-phase voltage drop value  in  Table 42 or Table 45 by   1.155.

- These ratings are based on  30°C  ambient  air  temperature  and  15°C  ambient  soil  temperature.  For  other  conditions,  see  Clause 3.5.3.

COPYRIGHT

AS/NZS 3008.1.2:1998	42

### TABLE	11

CURRENT-CARRYING CAPACITIES OF TWO-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED) CABLES   WITH

OR WITHOUT EARTH CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH  R-HF-110,

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

R-E-110 OR X-HF-110  INSULATION

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor size mm2 | Current-carrying capacity, A |  |  |  |  |  |  |
|  | Unenclosed |  | Enclosed |  |  | Buried direct | Underground non- metallic wiring enclosure |
|  | Spaced | Touching | Metallic | In metallic wiring | Completely |  |  |
|  |  |  | wiring | enclosure unenclosed | surrounded by |  |  |
|  |  |  | enclosure in | partially surrounded | thermal |  |  |
|  |  |  | air | by thermal | insulation |  |  |
|  |  |  |  | insulation |  |  |  |
|  | Cu | Cu | Cu | Cu | Cu | Cu | Cu |
| 1 | 25 | 24 | 20 | 16 | 12 | 31 | 24 |
| 1.5 | 31 | 30 | 26 | 20 | 15 | 39 | 31 |
| 2.5 | 44 | 42 | 35 | 29 | 20 | 54 | 42 |
| 4 | 59 | 55 | 48 | 39 | 28 | 71 | 55 |
| 6 | 74 | 70 | 60 | 48 | 35 | 89 | 69 |
| 10 | 102 | 95 | 81 | 64 | 48 | 117 | 92 |
| 16 | 134 | 128 | 107 | 87 | 63 | 154 | 122 |
| 25 | 182 | 171 | 144 | 112 | 85 | 201 | 159 |
| 35 | 219 | 209 | 177 | 144 | 104 | 239 | 191 |
| 50 | 268 | 251 | 214 | 171 | — | 286 | 228 |
| 70 | 337 | 321 | 273 | 219 | — | 350 | 281 |
| 95 | 417 | 391 | 332 | 268 | — | 419 | 339 |
| 120 | 487 | 455 | 396 | 316 | — | 477 | 392 |
| 150 | 556 | 519 | 444 | 358 | — | 541 | 445 |
| 185 | 642 | 599 | 519 | 417 | — | 604 | 509 |
| 240 | 760 | 706 | 631 | 503 | — | 700 | 604 |
| 300 | 867 | 813 | 717 | 578 | — | 795 | 678 |
| 400 | 1006 | 942 | 824 | 653 | — | 901 | 774 |
| 500 | 1145 | 1070 | 963 | 770 | — | 1018 | 901 |

NOTES:

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for cable configurations deemed to have the same current-carrying capacities as those illustrated.

- Derating factors may apply as   follows:

  - The  current-carrying capacities apply to  single circuits; for  grouped cable circuits see  Clause 3.5.2 and  Tables 22,  24,  25   and 26  for appropriate derating  factors.

  - For a  single circuit fixed to  the underside of  a  ceiling or  similar horizontal surface, see Table 22  for the derating factor to      be  applied to  the current-carrying capacities given in  Column  3.

  - For a single circuit fixed to unperforated cable tray, see Table 24  for  the  derating  factor  to  be  applied  to  the  current- carrying capacities given in  Column  2.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To calculate the single-phase voltage drop of these configurations,  multiply the  appropriate three-phase voltage drop  value in  Table 42 or Table 45 by   1.155.

- These ratings are based on  30°C  ambient  air  temperature  and  15°C  ambient  soil  temperature.  For  other  conditions,  see  Clause 3.5.3.

COPYRIGHT

43	AS/NZS 3008.1.2:1998

### TABLE	12

CURRENT-CARRYING CAPACITIES OF THREE-CORE AND FOUR-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED)   CABLES

WITH OR WITHOUT EARTH CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH V-75,  V-90,

HFI-75-TP OR HFI-90-TP INSULATION (See Note   1)

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Unenclosed |  |  |  | Enclosed |  |  |  |  |  |  |  | Buried direct |  | Underground non-metallic wiring enclosure |  |
|  | Spaced |  | Touching |  | Non- |  | Non-metallic |  | In non-metallic |  | Completely |  |  |  |  |  |
|  |  |  |  |  | metallic |  | wiring |  | wiring |  | surrounded by |  |  |  |  |  |
|  |  |  |  |  | wiring |  | enclosures in |  | enclosures or |  | thermal |  |  |  |  |  |
|  |  |  |  |  | enclosures |  | air — flat cable |  | unenclosed |  | insulation |  |  |  |  |  |
|  |  |  |  |  | in |  |  |  | partially |  |  |  |  |  |  |  |
| Con- ductor size |  |  |  |  | air — round cable |  |  |  | surrounded by thermal insulation |  |  |  |  |  |  |  |
| mm2 | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 1 | 15 | — | 14 | — | 11 | 9 | 14 | 10 | 11 | 8 | 7 | — | 21 | — | 17 | — |
| 1.5 | 18 | — | 17 | — | 15 | 11 | 17 | 13 | 14 | 11 | 9 | — | 26 | — | 21 | — |
| 2.5 | 26 | — | 25 | — | 21 | 16 | 23 | 17 | 19 | 15 | 13 | — | 37 | — | 29 | — |
| 4 | 35 | — | 33 | — | 27 | 21 | 30 | 23 | 25 | 19 | 17 | — | 48 | — | 37 | — |
| 6 | 46 | — | 42 | — | 35 | 27 | 39 | 30 | 33 | 25 | 22 | — | 61 | — | 47 | — |
| 10 | 62 | — | 58 | — | 48 | 38 | 52 | 40 | 44 | 34 | 29 | — | 81 | — | 63 | — |
| 16 | 82 | 64 | 78 | 60 | 64 | 49 | 68 | 52 | 59 | 46 | 39 | 30 | 106 | 83 | 81 | 64 |
| 25 | 111 | 86 | 104 | 81 | 90 | 68 | 95 | 72 | 82 | 64 | 52 | 40 | 138 | 107 | 106 | 83 |
| 35 | 137 | 106 | 125 | 99 | 105 | 80 | 105 | 80 | 96 | 74 | 64 | 49 | 165 | 127 | 127 | 100 |
| 50 | 165 | 131 | 154 | 120 | 125 | 96 | 125 | 96 | 114 | 90 | — | — | 198 | 154 | 154 | 121 |
| 70 | 211 | 165 | 194 | 154 | 160 | 120 | — | — | 143 | 113 | — | — | 242 | 187 | 193 | 149 |
| 95 | 262 | 205 | 245 | 188 | 188 | 143 | — | — | 171 | 137 | — | — | 292 | 226 | 231 | 182 |
| 120 | 302 | 234 | 279 | 222 | 222 | 171 | — | — | 200 | 160 | — | — | 330 | 259 | 264 | 209 |
| 150 | 348 | 268 | 319 | 251 | 257 | 194 | — | — | 228 | 182 | — | — | 369 | 292 | 297 | 231 |
| 185 | 399 | 314 | 371 | 291 | 296 | 222 | — | — | 262 | 205 | — | — | 418 | 330 | 341 | 270 |
| 240 | 467 | 371 | 439 | 348 | 348 | 262 | — | — | 308 | 245 | — | — | 484 | 380 | 407 | 319 |
| 300 | 536 | 428 | 502 | 399 | — | — | — | — | — | — | — | — | 545 | 429 | 457 | 358 |
| 400 | 616 | 502 | 570 | 462 | — | — | — | — | — | — | — | — | 616 | 495 | 528 | 424 |
| 500 | 707 | 570 | 650 | 524 | — | — | — | — | — | — | — | — | 682 | 550 | 594 | 479 |

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

NOTES:

- Refer to  Note 2  of  Table 1  for information regarding the use of  V-90 insulated  cables.

- Refer to Tables 2(1), 2(2),  2(3)  and  2(4)  for  cable  configurations  deemed  to  have  the  same  current-carrying  capacities  as  those illustrated.

- Derating factors may apply as   follows:

  - The  current-carrying capacities apply to  single circuits; for  grouped cable circuits see  Clause 3.5.2 and  Tables 22,  24, 25      and 26  for appropriate derating  factors.

  - For  a  single  circuit  fixed  to  the  underside  of  a  ceiling  or  similar  horizontal  surface,  see  Table  22  for  the  derating  factor  to be  applied  to  the  current-carrying  capacities  given  in  Columns  4  and 5.

  - For a single circuit fixed to unperforated cable tray, see Table 24  for  the  derating  factor  to  be  applied  to  the  current-  carrying capacities given in  Columns 2  and  3.

  - For ambient temperature and depth of  laying factors, see Tables 27  and    28.

- To  determine the three-phase voltage drop of  these configurations, refer to  the appropriate value in  Table 42  or  Table   45.

- These   ratings   are   based   on   30°C   ambient   air   temperature   and   15°C   ambient   soil   temperature.   For   other  conditions,   see Clause 3.5.3.

COPYRIGHT

AS/NZS 3008.1.2:1998	44

### TABLE	13

CURRENT-CARRYING CAPACITIES OF THREE-CORE AND FOUR-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING NEUTRAL SCREENED)   CABLES

WITH OR WITHOUT EARTH CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH X-90,  X-HF-90,

R-EP-90, R-CPE-90, R-HF-90 OR R-CSP-90 INSULATION

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Unenclosed |  |  |  | Enclosed |  |  |  |  |  | Buried direct |  | Underground non-metallic wiring enclosure |  |
|  | Spaced |  | Touching |  | Non-metallic |  | In non-metallic |  | Completely |  |  |  |  |  |
|  |  |  |  |  | wiring enclosure |  | wiring enclosure |  | surrounded by |  |  |  |  |  |
|  |  |  |  |  | in air |  | or unenclosed |  | thermal |  |  |  |  |  |
|  |  |  |  |  |  |  | partially |  | insulation |  |  |  |  |  |
|  |  |  |  |  |  |  | surrounded by |  |  |  |  |  |  |  |
| Con- |  |  |  |  |  |  | thermal |  |  |  |  |  |  |  |
| ductor |  |  |  |  |  |  | insulation |  |  |  |  |  |  |  |
| size |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| mm2 | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al | Cu | Al |
| 1 | 18 | — | 15 | — | 13 | 10 | 13 | 11 | 8 | — | 24 | — | 18 | — |
| 1.5 | 22 | — | 21 | — | 18 | 13 | 18 | 14 | 10 | — | 30 | — | 22 | — |
| 2.5 | 31 | — | 29 | — | 24 | 19 | 23 | 19 | 14 | — | 42 | — | 32 | — |
| 4 | 42 | — | 39 | — | 32 | 24 | 31 | 25 | 20 | — | 55 | — | 41 | — |
| 6 | 53 | — | 50 | — | 42 | 32 | 40 | 32 | 24 | — | 67 | — | 51 | — |
| 10 | 73 | — | 68 | — | 58 | 44 | 55 | 44 | 34 | — | 91 | — | 68 | — |
| 16 | 97 | 75 | 91 | 70 | 77 | 59 | 73 | 58 | 45 | 35 | 118 | 91 | 89 | 70 |
| 25 | 132 | 102 | 121 | 95 | 108 | 84 | 101 | 80 | 62 | 47 | 155 | 118 | 118 | 91 |
| 35 | 160 | 127 | 149 | 116 | 127 | 98 | 116 | 94 | 76 | 58 | 182 | 144 | 144 | 112 |
| 50 | 198 | 154 | 187 | 143 | 154 | 121 | 143 | 110 | — | — | 219 | 171 | 171 | 134 |
| 70 | 253 | 198 | 237 | 182 | 193 | 149 | 176 | 143 | — | — | 268 | 209 | 214 | 166 |
| 95 | 314 | 242 | 292 | 226 | 231 | 182 | 215 | 171 | — | — | 321 | 251 | 257 | 198 |
| 120 | 363 | 281 | 336 | 264 | 275 | 215 | 248 | 198 | — | — | 369 | 284 | 294 | 230 |
| 150 | 413 | 325 | 385 | 297 | 308 | 242 | 281 | 226 | — | — | 412 | 321 | 332 | 257 |
| 185 | 479 | 374 | 446 | 347 | 358 | 281 | 325 | 259 | — | — | 465 | 364 | 380 | 300 |
| 240 | 572 | 446 | 528 | 413 | 424 | 336 | 385 | 303 | — | — | 535 | 423 | 449 | 353 |
| 300 | 649 | 512 | 605 | 473 | — | — | — | — | — | — | 610 | 476 | 508 | 401 |
| 400 | 748 | 605 | 693 | 550 | — | — | — | — | — | — | 685 | 546 | 578 | 460 |
| 500 | 858 | 693 | 792 | 638 | — | — | — | — | — | — | 760 | 621 | 663 | 535 |

NOTES:

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for cable configurations deemed to have the same current-carrying capacities as those illustrated.

- Derating factors may apply as   follows:

  - The  current-carrying capacities apply to  single circuits; for  grouped cable circuits see  Clause 3.5.2 and  Tables 22,  24,  25   and 26  for appropriate derating  factors.

  - For a  single circuit fixed to  the underside of  a  ceiling or  similar horizontal surface, see Table 22  for the derating factor to      be  applied to  the current-carrying capacities given in  Columns 4  and  5.

  - For a single circuit fixed to unperforated cable tray, see Table 24  for  the  derating  factor  to  be  applied  to  the  current- carrying capacities given in Columns 2 and   3.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To  determine the three-phase voltage drop of  these configurations, refer to  the appropriate value in  Table 42  or  Table   45.

- These ratings are based on  30°C  ambient  air  temperature  and  15°C  ambient  soil  temperature.  For  other  conditions,  see  Clause 3.5.3.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

45	AS/NZS 3008.1.2:1998

### TABLE	14

CURRENT-CARRYING CAPACITIES OF THREE-CORE AND FOUR-CORE 0.6/1 kV INSULATED AND SHEATHED (INCLUDING   NEUTRAL

SCREENED) CABLES WITH OR WITHOUT EARTH CONDUCTOR, ARMOURED OR NON-ARMOURED CABLES WITH  R-HF-110,

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

R-E-110 OR X-HF-110  INSULATION

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor size mm2 | Current-carrying capacity, A |  |  |  |  |  |  |
|  | Unenclosed |  | Enclosed |  |  | Buried direct | Underground non-metallic wiring enclosure |
|  | Spaced | Touching | Metallic | In metallic wiring | Completely |  |  |
|  |  |  | wiring | enclosure | surrounded by |  |  |
|  |  |  | enclosure in | unenclosed partially | thermal insulation |  |  |
|  |  |  | air | surrounded by |  |  |  |
|  |  |  |  | thermal insulation |  |  |  |
|  | Cu | Cu | Cu | Cu | Cu | Cu | Cu |
| 1 | 21 | 19 | 17 | 14 | 10 | 27 | 20 |
| 1.5 | 27 | 26 | 21 | 17 | 13 | 33 | 25 |
| 2.5 | 37 | 35 | 31 | 25 | 18 | 47 | 36 |
| 4 | 50 | 47 | 41 | 32 | 24 | 59 | 47 |
| 6 | 63 | 60 | 50 | 41 | 30 | 75 | 58 |
| 10 | 87 | 81 | 68 | 55 | 41 | 100 | 77 |
| 16 | 112 | 107 | 92 | 73 | 54 | 127 | 101 |
| 25 | 155 | 144 | 123 | 100 | 72 | 170 | 133 |
| 35 | 187 | 177 | 150 | 118 | 89 | 201 | 159 |
| 50 | 230 | 214 | 187 | 150 | — | 239 | 191 |
| 70 | 289 | 273 | 230 | 187 | — | 292 | 239 |
| 95 | 358 | 337 | 289 | 230 | — | 355 | 292 |
| 120 | 417 | 391 | 332 | 268 | — | 403 | 329 |
| 150 | 476 | 444 | 385 | 310 | — | 451 | 376 |
| 185 | 546 | 514 | 439 | 353 | — | 509 | 424 |
| 240 | 653 | 610 | 535 | 428 | — | 594 | 504 |
| 300 | 749 | 696 | — | — | — | 668 | 572 |
| 400 | 867 | 803 | — | — | — | 753 | 668 |
| 500 | 995 | 920 | — | — | — | 848 | 753 |

NOTES:

- Refer to Tables 2(1), 2(2), 2(3) and 2(4) for cable configurations deemed to have the same current-carrying capacities as those illustrated.

- Derating factors may apply as   follows:

  - The current-carrying capacities apply to  single circuits; for grouped cable circuits see Clause 3.5.2 and Tables 22, 24, 25      and 26  for appropriate derating  factors.

  - For a  single circuit fixed to  the underside of  a  ceiling or  similar horizontal surface, see Table 22  for the derating factor to   be  applied to  the current-carrying capacities given in  Column  3.

  - For a single circuit fixed to  unperforated cable tray, see Table 24  for the derating factor to  be  applied to  the current-  carrying capacities given in  Column  2.

  - For ambient temperature and depth of laying factors, see Tables 27 and 28.

- To  determine the three-phase voltage drop of  these configurations, refer to  the appropriate value in  Table 42  or  Table   45.

- These ratings are based on  30°C  ambient  air  temperature  and  15°C  ambient  soil  temperature.For  other  conditions,  see  Clause 3.5.3.

COPYRIGHT

AS/NZS 3008.1.2:1998	46

### TABLE	15

CURRENT-CARRYING CAPACITIES OF 0.6/1 kV FLEXIBLE   CABLES

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor size mm2 | Current-carrying capacity, A |  |  |  |  |  |  |  |
|  | Single- and two-core |  |  |  | Three- and four-core (see Note 3) |  |  |  |
|  | Protected from sun |  | Exposed to sun |  | Protected from sun |  | Exposed to sun |  |
|  | V75, V90 | R-EP-90 R-CSP-90 | V75, V90 | R-EP-90 R-CSP-90 | V75, V90 | R-EP-90 R-CSP-90 | V75, V90 | R-EP-90 R-CSP-90 |
| 6 | 50 | 59 | 39 | 47 | 43 | 51 | 33 | 41 |
| 10 | 68 | 81 | 52 | 64 | 59 | 69 | 44 | 55 |
| 16 | 92 | 109 | 68 | 85 | 80 | 94 | 58 | 73 |
| 25 | 125 | 149 | 91 | 116 | 108 | 127 | 78 | 97 |
| 35 | 154 | 182 | 108 | 138 | 131 | 154 | 92 | 116 |
| 50 | 182 | 215 | 125 | 160 | 160 | 182 | 109 | 138 |
| 70 | 234 | 275 | 160 | 204 | 200 | 237 | 137 | 171 |
| 95 | 274 | 319 | 182 | 231 | 234 | 275 | 160 | 198 |
| 120 | 319 | 374 | 211 | 270 | 274 | 319 | 182 | 231 |
| 150 | 365 | 429 | 245 | 308 | 319 | 369 | 211 | 264 |
| 185 | 410 | 484 | 274 | 347 | 359 | 418 | 234 | 297 |
| 240* | 485 | 561 | 314 | 402 | 422 | 490 | 268 | 341 |
| 300* | 559 | 660 | 359 | 462 | 485 | 561 | 308 | 396 |
| 400* | 673 | 792 | 428 | 550 | 581 | 682 | 371 | 468 |
| 500† | 752 | 880 | 473 | 616 | — | — | — | — |

*    Single-core, two-core and three-core  only.

†     Single-core, only.

NOTES:

- The number of wires and the nominal diameter of each wire is given in AS 1125. The ratings apply to  conductors having a large number of smaller wires than specified in AS 1125.

- Where layers of flexible cable are accommodated on a  cylindrical-type  cable  drum  or  reel,  multiply  the values in Columns 2 to 9 by the appropriate factor, as follows:

Number of layers: 1	2	3	4

Derating factor:	0.85	0.65	0.45	0.35

Where a spiral layer of flexible cable is accommodated on a radial-type cable drum, multiply the values in Columns 2 to 9 by a factor of 0.85 for ventilated drums and 0.75 for unventilated drums.

- The current-carrying capacities may also be applied to flat cables with three or four loaded conductors.

- To determine  the  three-phase  voltage  drop  of  these  configurations,  refer  to  the  appropriate  value  in  Table 46 or Table 47. To determine the single-phase voltage drop, multiply the three-phase value by 1.155.

- These ratings are based on 30°C ambient air temperature. For other conditions, see Clause 3.5.3.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

47	AS/NZS 3008.1.2:1998

### TABLE	16

CURRENT-CARRYING CAPACITIES OF FLEXIBLE  CORDS

| 1 | 2 |
| --- | --- |
| Conductor size mm2 | Current-carrying capacity A |
| 0.5 | 3 (see Note 3) |
| 0.75 | 7.5 |
| 1.0 | 10 |
| 1.5 | 16 |
| 2.5 | 20 |
| 4.0 | 25 |

NOTES:

  - The minimum number of wires in each conductor is given in AS 1125. The current-carrying capacity also applies to  conductors having a  larger number     of smaller wires.

  - Where a flexible cord is  wound on  a  drum, multiply current-carrying capacity by  the appropriate factor, as  follows:

Number of layers:	1	2	3	4

Derating factor:	0.76	0.58	0.47	0.40

  - Flexible cords  having  tinsel  conductors  with  a  nominal  cross-sectional  area of  0.5 mm2 have a  current-carrying capacity of  0.5  A.

  - The current-carrying capacity is based on a cable maximum  conductor  operating temperature of  60°C in  order to  limit the surface temperatures for   the expected use of  such cables. See Clause 3.3.2.1 where flexible cords are  used as fixed wiring and higher temperatures are    permitted.

  - To determine the three-phase voltage drop, refer to the appropriate value in  Table 48 or  Table 49.  To  determine the  single-phase voltage drop, multiply  the three-phase value by  1.155.

  - These ratings are based on 25°C ambient air    temperature.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	48

### TABLE	17

CURRENT-CARRYING CAPACITIES OF CABLES AND FLEXIBLE CORDS WITH R-S-150, TYPE 150 FIBROUS OR 150 TYPE PTFE    INSULATION

| 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- |
| Conductor size mm2 | Current-carrying capacity, A |  |  |  |
|  | Two single-core or one two-core |  | Three or four single-core or three or four core |  |
|  | Unenclosed in air | Enclosed in air | Unenclosed in air | Enclosed in air |
| 0.5 | 20 | 16 | 16 | 14 |
| 0.75 | 25 | 21 | 21 | 17 |
| 1.0 | 29 | 24 | 25 | 20 |
| 1.5 | 38 | 29 | 32 | 25 |
| 2.5 | 52 | 40 | 45 | 33 |
| 4 | 70 | 52 | 60 | 44 |
| 6 | 90 | 70 | 77 | 57 |
| 10 | 125 | 94 | 109 | 79 |
| 16 | 172 | 124 | 146 | 103 |
| 25 | 224 | 166 | 192 | 140 |
| 35 | 276 | 202 | 239 | 170 |

NOTES:

- The values are based on a conductor maximum operating temperature of 150°C and an ambient air temperature of 30°C. Where cables are to be operated at this temperature, care must be taken to avoid inadvertent contact with the hot  surface  of  the  cable  and  associated  supports  and  terminations,  and also to  avoid subjecting the cable to  mechanical stresses. Where cables are not operated in  an  ambient  air temperature of 30°C, reference must be made to the appropriate rating factors in Table 27.1.

- As a conservative alternative to cable manufacturers’ recommendations, the values given in this Table  may also be applied to fibrous or PTFE insulated  cables  designed  for  a  maximum  operating  temperature of  200°C.

- No values are given in Clause 4 for voltage drop for these  types  of  cable  as  they  are  generally  installed for relatively short connections to high  temperature  equipment.  However,  on  longer  cable runs, as the increase in conductor impedance at 150°C is considerable, it  may be  necessary to  take  voltage drop into  account.

- These ratings are based on 30°C ambient air temperature. For other conditions, see Clause 3.5.3.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

49	AS/NZS 3008.1.2:1998

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

TABLE	18

CURRENT-CARRYING CAPACITIES OF BARE SINGLE-CORE MINERAL-INSULATED COPPER-SHEATHED CABLES

WITH COPPER CONDUCTORS— SHEATH TEMPERATURE: 100°C

| 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| --- | --- | --- | --- | --- | --- | --- |
| Conductor size mm2 | Current-carrying capacity, A |  |  |  |  |  |
|  | Vertical spaced — spaced from wall | Flat horizontal — spaced from wall | Flat vertical — clipped to wall | Vertical spaced — spaced from wall | Trefoil — spaced from wall | Flat vertical — clipped to wall |

0.6/0.6 kV cables

| 1 | 23 | 20 | 18 | 20 | 18 | 16 |
| --- | --- | --- | --- | --- | --- | --- |
| 1.5 | 27 | 25 | 22 | 26 | 22 | 20 |
| 2.5 | 38 | 34 | 30 | 37 | 30 | 28 |
| 4 | 51 | 46 | 41 | 48 | 41 | 37 |

1/1 kV cables

| 1.5 | 33 | 29 | 26 | 32 | 26 | 24 |
| --- | --- | --- | --- | --- | --- | --- |
| 2.5 | 42 | 39 | 35 | 42 | 35 | 32 |
| 4 | 59 | 52 | 47 | 56 | 47 | 43 |
| 6 | 74 | 66 | 60 | 74 | 60 | 54 |
| 10 | 100 | 91 | 82 | 97 | 82 | 74 |
| 16 | 140 | 120 | 110 | 130 | 110 | 100 |
| 25 | 175 | 165 | 145 | 170 | 145 | 135 |
| 35 | 215 | 200 | 180 | 210 | 180 | 165 |
| 50 | 280 | 255 | 225 | 270 | 225 | 205 |
| 70 | 350 | 315 | 285 | 340 | 285 | 260 |
| 95 | 410 | 370 | 235 | 400 | 340 | 305 |
| 120 | 480 | 435 | 390 | 465 | 400 | 355 |
| 150 | 565 | 505 | 455 | 540 | 465 | 415 |
| 185 | 660 | 595 | 535 | 635 | 545 | 485 |
| 240 | 790 | 710 | 640 | 755 | 650 | 580 |
| 300 | 875 | 795 | 710 | 850 | 745 | 650 |
| 400 | 1090 | 985 | 885 | 1050 | 920 | 805 |

NOTES:

- The current-carrying capacities given in  this Table are based on  a  maximum operating temperature of  100°C for   the external surface of the bare copper sheath. The current-carrying capacities of served cables may be 1.1 times higher than these if  they are served with a  material which is  suitable for a  copper sheath temperature of  105°C.  See Clause 3.2.2 and  Table 1  for conditions where higher cable operating temperatures may be  permitted for      bare sheathed cables.

- To determine the three-phase voltage drop, refer to  the appropriate value in  Table 48. To  determine the single-  phase voltage drop, multiply the three-phase value by    1.155.

- The current-carrying capacities apply to  single circuits. For grouped cable circuits    see—

  - Clause 3.5.2 and Tables 22 to 26 for derating factors for served cables; and

  - Clause 3.5.2.2(a) for the treatment of unserved   cables.

- For earth sheath return system, temperature rises could be higher. Refer to manufacturer.

- These ratings are based on 30°C ambient air temperature. For other conditions, see Clause 3.5.3.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	50

### TABLE	19

CURRENT-CARRYING CAPACITIES OF BARE MULTICORE MINERAL-INSULATED COPPER-SHEATHED

CABLES WITH COPPER CONDUCTORS— SHEATH TEMPERATURE: 100°C

| 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| --- | --- | --- | --- | --- | --- | --- |
| Conductor size mm2 | Current-carrying capacity, A |  |  |  |  |  |
|  | Two core — spaced from wall | Two core — clipped to wall | Three and four core — spaced from wall | Three and four core — clipped to wall | Seven core — spaced from wall | Seven core — clipped to wall |

0.6/0.6 kV cables

| 1 | 19 | 17 | 17 | 16 | 12 | 11 |
| --- | --- | --- | --- | --- | --- | --- |
| 1.5 | 25 | 23 | 21 | 19 | 16 | 15 |
| 2.5 | 34 | 31 | 29 | 28 | 22 | 21 |
| 4 | 46 | 43 | — | — | — | — |

1/1 kV cables

| 1.5 | 29 | 27 | 24 | 23 | 18 | 17 |
| --- | --- | --- | --- | --- | --- | --- |
| 2.5 | 38 | 35 | 32 | 30 | 24 | 22 |
| 4 | 51 | 47 | 43 | 41 | 32 | 30 |
| 6 | 66 | 62 | 55 | 52 | — | — |
| 10 | 91 | 84 | 77 | 73 | — | — |
| 16 | 125 | 115 | 105 | 96 | — | — |
| 25 | 165 | 155 | 140 | 135 | — | — |

NOTES:

- The  current-carrying capacities given in  this Table are  based on  a  maximum operating temperature    of 100°C for the external surface of the  bare  copper  sheath.  The  current-carrying  capacities  of  served cables may be 1.1 times higher than these if  they are served with a  material which is  suitable  for a copper sheath temperature of 105°C. See Clause 3.2.2 and Table 1 for conditions where higher cable operating temperatures may be    permitted for bare sheathed cables.

- To  determine the three-phase voltage drop, refer to  the appropriate value in  Table 48. To  determine  the single-phase voltage drop, multiply the three-phase value by 1.155.

- The current-carrying capacities apply to  single circuits. For grouped cable circuits    see—

  - Clause 3.5.2 and Tables 22 to 26 for derating factors for served cables; and

  - Clause 3.5.2.2(a) for the treatment of unserved   cables.

- For earth sheath return system, temperature rises could be higher. Refer to manufacturer.

- These ratings are based on 30°C ambient air temperature. For other conditions, see Clause 3.5.3.

COPYRIGHT

Copyright Standards New Zealand Provided by IHS under license with SNZ

No reproduction or networking permitted without license from IHS

51	AS/NZS 3008.1.2:1998

### TABLE	20

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Licensee=Unitec Inst of Technology/5911177001 Not for Resale, 02/25/2009 13:29:58 MST

CURRENT-CARRYING CAPACITIES OF AERIAL CABLES WITH COPPER CONDUCTORS

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor size, mm2, or stranding (No./mm) | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |
|  | Bare conductors |  |  | PVC insulated single-core |  |  | PVC insulated two-core twisted, two-core neutral screened and two-core or three-core parallel webbed cable |  |  | PVC insulated three-core and four-core twisted and three-core or four-core neutral screened cable |  |  |
|  | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind |
| 7/1.00 | 42 | 85 | 100 | — | — | — | — | — | — | — | — | — |
| 6 | 43 | 86 | 102 | 40 | 80 | 90 | 34 | 57 | 67 | 30 | 55 | 64 |
| 7/1.25 | 56 | 111 | 131 | — | — | — | — | — | — | — | — | — |
| 10 | 60 | 119 | 141 | 55 | 109 | 125 | 46 | 78 | 91 | 41 | 74 | 87 |
| 16 | 81 | 159 | 187 | 74 | 143 | 165 | 59 | 103 | 120 | 54 | 97 | 114 |
| 7/1.75 | 86 | 169 | 199 | — | — | — | — | — | — | — | — | — |
| 7/2.00 | 102 | 198 | 234 | — | — | — | — | — | — | — | — | — |
| 25 | 110 | 212 | 251 | 100 | 188 | 217 | 78 | 137 | 160 | 72 | 131 | 154 |
| 35 | 133 | 258 | 304 | 120 | 234 | 262 | 93 | 165 | 194 | 87 | 154 | 182 |
| 7/2.75 | 152 | 293 | 345 | — | — | — | — | — | — | — | — | — |
| 50 | 162 | 310 | 366 | 148 | 274 | 314 | 111 | 200 | 234 | 105 | 188 | 217 |
| 19/1.75 | 162 | 311 | 367 | — | — | — | — | — | — | — | — | — |
| 19/2.00 | 191 | 366 | 432 | — | — | — | — | — | — | — | — | — |
| 70 | 204 | 389 | 459 | 188 | 348 | 393 | 137 | 245 | 291 | 131 | 234 | 274 |
| 7/3.50 | 206 | 393 | 464 | — | — | — | — | — | — | — | — | — |
| 7/3.75 | 225 | 428 | 506 | — | — | — | — | — | — | — | — | — |
| 95 | 246 | 467 | 552 | 228 | 410 | 473 | — | — | — | — | — | — |
| 37/1.75 | 246 | 468 | 553 | — | — | — | — | — | — | — | — | — |

(continued)

Copyright Standards New Zealand Provided by IHS under license with SNZ

No reproduction or networking permitted without license from IHS

AS/NZS 3008.1.2:1998	52

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

TABLE	20	(continued)

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor size, mm2, or stranding (No./mm) | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |
|  | Bare conductors |  |  | PVC insulated single-core |  |  | PVC insulated two-core twisted, two-core neutral screened and two-core or three-core parallel webbed cable |  |  | PVC insulated three-core and four-core twisted and three-core or four-core neutral screened cable |  |  |
|  | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind |
| 19/2.75 | 286 | 541 | 639 | — | — | — | — | — | — | — | — | — |
| 120 | 290 | 548 | 648 | 268 | 485 | 553 | — | — | — | — | — | — |
| 19/3.00 | 320 | 602 | 712 | — | — | — | — | — | — | — | — | — |
| 150 | 331 | 623 | 737 | 302 | 542 | 627 | — | — | — | — | — | — |
| 185 | 383 | 716 | 846 | 353 | 616 | 707 | — | — | — | — | — | — |
| 37/2.50 | 387 | 723 | 855 | — | — | — | — | — | — | — | — | — |

Licensee=Unitec Inst of Technology/5911177001 Not for Resale, 02/25/2009 13:29:58 MST

NOTES:

- The current-carrying capacities are based on  an  ambient air temperature of  30°C, a  maximum conductor temperature of  75°C and exposure to  direct sunlight having an   intensity of 1000 W/m2. In addition the values for bare conductors are based on  black (weathered) conductors and the values of  insulated conductors are based on the use             of black PVC.

- Under normal circumstances there will always be some air movement and a minimum rating for 1.0 m/s wind is recommended.

- To  determine the three-phase voltage drop of  these configurations, refer to  the following   Tables:

  - For twisted cables, see Table  40.

  - For parallel and webbed cables, see Table   41.

  - For bare and single insulated cables, see Table    49.

- These ratings are based on 30°C ambient air temperature. For other conditions, see Clause 3.5.3.

Copyright Standards New Zealand Provided by IHS under license with SNZ

No reproduction or networking permitted without license from IHS

Licensee=Unitec Inst of Technology/5911177001 Not for Resale, 02/25/2009 13:29:58 MST

53	AS/NZS 3008.1.2:1998

### TABLE	21

CURRENT-CARRYING CAPACITIES OF AERIAL AND ABC CABLES WITH ALUMINIUM  CONDUCTORS

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor size, mm2, or stranding (No./mm) | Current-carrying capacity, A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Bare conductors |  |  | PVC insulated single-core |  |  | PVC insulated two-core twisted, two-core neutral screened and two-core or three-core parallel webbed cable |  |  | PVC insulated three-core and four-core twisted and three-core or four- core neutral screened cable |  |  | XLPE insulated two-core twisted cable and ABC |  |  | XLPE insulated three- core and four-core twisted cable and ABC |  |  |
|  | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind | Still air | 1 m/s wind | 2 m/s wind |
| 16 | 63 | 124 | 146 | 56 | 111 | 125 | 47 | 81 | 96 | 41 | 75 | 88 | 55 | 87 | 102 | 49 | 83 | 96 |
| 25 | 86 | 167 | 197 | 76 | 148 | 165 | 60 | 104 | 125 | 55 | 99 | 114 | 72 | 118 | 134 | 66 | 109 | 129 |
| 35 | 105 | 202 | 239 | 93 | 177 | 205 | 72 | 125 | 148 | 67 | 120 | 143 | 87 | 140 | 162 | 81 | 134 | 151 |
| 7/2.50 | 106 | 205 | 242 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — |
| 7/2.75 | 120 | 231 | 273 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — |
| 50 | 127 | 244 | 288 | 113 | 211 | 245 | 86 | 154 | 182 | 81 | 143 | 171 | 105 | 168 | 202 | 99 | 157 | 185 |
| 7/3.00 | 134 | 257 | 303 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — |
| 70 | 160 | 306 | 361 | 143 | 268 | 302 | 105 | 188 | 228 | 101 | 177 | 211 | 129 | 213 | 252 | 123 | 196 | 230 |
| 7/3.75 | 178 | 338 | 399 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — |
| 95 | 194 | 367 | 434 | 177 | 319 | 371 | 125 | 234 | 279 | 125 | 217 | 262 | 157 | 258 | 308 | 151 | 241 | 286 |
| 7/4.50 | 223 | 422 | 499 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — |
| 120 | 228 | 431 | 510 | 205 | 371 | 428 | — | — | — | — | — | — | — | — | — | 174 | 280 | 336 |
| 7/4.75 | 239 | 451 | 533 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — |
| 150 | 260 | 489 | 578 | 234 | 416 | 479 | — | — | — | — | — | — | — | — | — | 202 | 314 | 386 |
| 19/3.25 | 278 | 523 | 618 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — |
| 185 | 301 | 563 | 665 | 274 | 479 | 547 | — | — | — | — | — | — | — | — | — | — | — | — |
| 19/3.50 | 307 | 574 | 678 | — | — | — | — | — | — | — | — | — | — | — | — | — | — | — |

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	54

NOTES TO TABLE  21:

- The current-carrying capacities are based on an ambient air temperature of 30°C, a maximum conductor temperature of  75°C for  PVC  or  80°C for  XLPE, and  exposure to  direct sunlight having an  intensity of  1000 W/m2. In addition the values for bare conductors are based on  black (weathered) conductors and the  values for insulated conductors are based on the use of black PVC or XLPE.

- Under normal circumstances there will always be  some air movement and a  minimum rating for 1.0 m/s     wind is recommended.

- To  determine the three-phase voltage drop of  these configurations, refer to  the following   Tables:

  - For twisted cables, see Table  43.

  - For parallel and webbed cables, see Table   44.

  - For bare and single insulated cables, see Table    50.

- These ratings are based on 30°C ambient air temperature. For other conditions, see Clause 3.5.3.

COPYRIGHT

55	AS/NZS 3008.1.2:1998

### TABLE	22

DERATING FACTORS FOR BUNCHED CIRCUITS OF SINGLE-CORE OR MULTICORE CABLES IN AIR OR IN WIRING   ENCLOSURES

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item No. | Arrangement of cables (see Notes 1 & 2) |  | Derating factors |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Number of circuits |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 12 | 14 | 16 | 18 | 20 or more |
| 1 | Bunched in air |  | 1.00 | 0.87 | 0.75 | 0.72 | 0.70 | 0.67 | — | — | — | — | — | — | — | — | — |
| 2 | Bunched on a surface or enclosed |  | 1.00 | 0.80 | 0.70 | 0.65 | 0.60 | 0.57 | 0.54 | 0.52 | 0.50 | 0.48 | 0.45 | 0.43 | 0.41 | 0.39 | 0.38 |
| 3 | Single layer on wall or floor | Touching | 1.00 | 0.85 | 0.79 | 0.75 | 0.73 | 0.72 | 0.72 | 0.71 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 | 0.70 |
| 4 |  | Spaced (see Notes 5 & 6) | 1.00 | 0.94 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |
| 5 | Single layer under ceiling | Touching | 0.95 | 0.81 | 0.72 | 0.68 | 0.66 | 0.64 | 0.63 | 0.62 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 | 0.61 |
| 6 |  | Spaced (see Notes 5 & 6) | 0.95 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 |

NOTES:

- Where the cable in the arrangements shown in Columns 2 and 3 consist of n loaded conductors, the conductors may be considered as—

  - groups of two loaded conductors;   or

  - groups of three loaded  conductors.

- Earthing conductors, lightly loaded neutral conductors of three-phase circuits and conductors subject only to momentary loading, such as control wiring, are not taken into account when considering the number of circuits.

- These factors are based on  uniform groups of  cables, equally loaded. In  accordance with Clause 3.5.6 the factors for  circuits subject to  intermittent or  varying loads may be   higher.

- These factors are applicable to numbers of circuits comprising the following:

  - Groups of two, three or four single-core   cables.

  - Multicore cables.

  - Cables passing more than once through the same group of  cables or  wiring enclosures and circuits connected in   parallel in accordance with Clause   3.5.2.7.

- ‘Spaced’ means a clearance of one cable diameter between cable  surfaces  of  adjacent  cables.  Where  the  cables  concerned are not of the same size, the spacing will be based on the largest cable diameter in the adjacent groups.

- No  derating factor is  applicable for the minimum spacings specified in  Clause 3.5.2.2(c) and Figure    1.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

AS/NZS 3008.1.2:1998	56

### TABLE	23

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

DERATING FACTORS FOR CIRCUITS OF SINGLE-CORE CABLES INSTALLED IN TRAYS, RACKS, CLEATS, OR OTHER SUPPORTS IN   AIR

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Item No. | Installation |  | Number of tiers or rows of cable supports | Arrangements of cables in a circuit (see Note 1) | Derating factors |  |  |
|  |  |  |  |  | Number of circuits per tier or row |  |  |
|  |  |  |  |  | 1 | 2 | 3 |
| 1 | Unperforated trays | (See Note 6) | 1 | 2 or 3 cables in horizontal formation | 0.95 | 0.85 | 0.84 |
| 2 |  |  | 2 |  | 0.92 | 0.83 | 0.79 |
| 3 |  |  | 3 |  | 0.91 | 0.82 | 0.76 |
| 4 | Perforated trays | (See Note 6) | 1 | 2 or 3 cables in horizontal formation | 0.97 | 0.89 | 0.87 |
| 5 |  |  | 2 |  | 0.94 | 0.85 | 0.81 |
| 6 |  |  | 3 |  | 0.93 | 0.84 | 0.79 |
| 7 | Ladder supports, racks and cleats | (See Note 6) | 1 | 2 or 3 cables in horizontal formation | 1.00 | 0.95 | 0.94 |
| 8 |  |  | 2 |  | 0.95 | 0.90 | 0.88 |
| 9 |  |  | 3 |  | 0.95 | 0.89 | 0.85 |
| 10 | Vertical perforated trays | (See Note 7) | 1 | 2 or 3 cables in vertical formation | 0.94 | 0.85 | — |
| 11 |  |  | 2 |  | 0.92 | 0.83 | — |
| 12 | Unperforated trays | (See Note 6) | 1 | 2 or 3 cables in horizontal formation | 0.98 | 0.96 | 0.94 |
| 13 |  |  | 2 |  | 0.95 | 0.91 | 0.87 |
| 14 |  |  | 3 |  | 0.94 | 0.90 | 0.85 |
| 15 | Perforated trays | (See Note 6) | 1 | 2 or 3 cables in horizontal formation | 1.00 | 0.98 | 0.96 |
| 16 |  |  | 2 |  | 0.97 | 0.93 | 0.89 |
| 17 |  |  | 3 |  | 0.96 | 0.92 | 0.86 |
| 18 | Ladder supports | (See Note 6) | 1 | 2 or 3 cables in horizontal formation | 1.00 | 1.00 | 1.00 |
| 19 |  |  | 2 |  | 0.97 | 0.95 | 0.93 |
| 20 |  |  | 3 |  | 0.97 | 0.94 | 0.90 |
| 21 | Vertical perforated trays | (See Note 7) | 1 | 2 or 3 cables in vertical formation | 1.00 | 0.91 | 0.89 |
| 22 |  |  | 2 |  | 1.00 | 0.90 | 0.86 |

NOTES:

- D  equals cable outside diameter or, in  the case of  a  flat multicore cable, the maximum dimension of  the   cable.

- Earthing conductors, lightly loaded neutral conductors of  three-phase circuits and conductors subject only        to  momentary loading, such as  control wiring, shall not be  taken into account when considering the number    of circuits.

- These derating factors are to be applied to groups of two, three or four single-core cables for which the current-carrying capacity for a single circuit is obtained from Columns 4 and 5 of  Tables 3,  4,  6  and 7,  Column 3 of Tables 5 and 8, and Tables 15 to 19.  The  factors are  also applicable to  groups of  single-core cables making up parallel circuits in    accordance with Clause 3.5.2.7.

- These factors are based on uniform groups of cables, equally loaded. In accordance with Clause  3.5.6, the factors for circuits subject to intermittent or varying loads may be higher.

COPYRIGHT

57	AS/NZS 3008.1.2:1998

- These factors are applicable to single layers  of  cables  or  trefoil  groups,  as  shown  in  Column  2.  Where there is more than one layer on the same tray or ladder support, Table 22 may be used.

- The vertical spacing of horizontal trays and  ladder  supports  shall  be  not  less  than  300  mm  (see  also  Figure 1).

- The horizontal spacing of vertical trays mounted back-to-back shall be not less than 230 mm.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

No derating factor is applicable for the minimum spacings specified in Clause 3.5.2.2(c) and Figure 1(a).

COPYRIGHT

AS/NZS 3008.1.2:1998	58

### TABLE	24

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

DERATING FACTORS FOR CIRCUITS OF MULTICORE CABLES INSTALLED IN TRAYS, RACKS, CLEATS OR OTHER SUPPORTS IN   AIR

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item No. | Installation |  | Number of tiers or rows of cable supports | Derating factors |  |  |  |  |  |
|  |  |  |  | Number of cables |  |  |  |  |  |
|  |  |  |  | 1 | 2 | 3 | 4 | 6 | 9 |
| 1 | Unperforated trays | Touching (see Note 6) | 1 | 0.97 | 0.85 | 0.78 | 0.75 | 0.71 | 0.68 |
| 2 |  |  | 2 | 0.97 | 0.84 | 0.76 | 0.73 | 0.68 | 0.63 |
| 3 |  |  | 3 | 0.97 | 0.83 | 0.75 | 0.72 | 0.66 | 0.61 |
| 4 |  | Spaced (see Note 6) | 1 | 0.97 | 0.96 | 0.94 | 0.93 | 0.90 | — |
| 5 |  |  | 2 | 0.97 | 0.95 | 0.92 | 0.90 | 0.86 | — |
| 6 |  |  | 3 | 0.97 | 0.94 | 0.91 | 0.89 | 0.84 | — |
| 7 | Perforated trays | Touching (see Note 6) | 1 | 1.00 | 0.88 | 0.82 | 0.78 | 0.76 | 0.73 |
| 8 |  |  | 2 | 1.00 | 0.87 | 0.80 | 0.76 | 0.73 | 0.68 |
| 9 |  |  | 3 | 1.00 | 0.86 | 0.79 | 0.75 | 0.71 | 0.66 |
| 10 |  | Spaced (see Note 6) | 1 | 1.00 | 1.00 | 0.98 | 0.95 | 0.91 | — |
| 11 |  |  | 2 | 1.00 | 0.99 | 0.96 | 0.92 | 0.87 | — |
| 12 |  |  | 3 | 1.00 | 0.98 | 0.95 | 0.91 | 0.85 | — |
| 13 | Ladder supports, racks and cleats | Touching (see Note 6) | 1 | 1.00 | 0.87 | 0.82 | 0.80 | 0.79 | 0.78 |
| 14 |  |  | 2 | 1.00 | 0.86 | 0.80 | 0.78 | 0.76 | 0.73 |
| 15 |  |  | 3 | 1.00 | 0.85 | 0.79 | 0.76 | 0.73 | 0.70 |
| 16 |  | Spaced (see Note 6) | 1 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | — |
| 17 |  |  | 2 | 1.00 | 0.99 | 0.98 | 0.97 | 0.96 | — |
| 18 |  |  | 3 | 1.00 | 0.98 | 0.97 | 0.96 | 0.93 | — |
| 19 | Vertical perforated trays | Touching (see Note 7) | 1 | 1.00 | 0.88 | 0.82 | 0.77 | 0.73 | 0.72 |
| 20 |  |  | 2 | 1.00 | 0.88 | 0.81 | 0.76 | 0.72 | 0.70 |
| 21 |  | Spaced (see Note 7) | 1 | 1.00 | 0.91 | 0.89 | 0.88 | 0.87 | — |
| 22 |  |  | 2 | 1.00 | 0.91 | 0.88 | 0.87 | 0.86 | — |

NOTES:

- D equals cable outside diameter or, in the case of a flat multicore cable, the maximum dimension of the cable.

- Earthing conductors, lightly loaded neutral conductors of three-phase circuits and conductors subject only to momentary loading, such as control wiring, shall not be taken into account when considering the number of circuits.

- These derating factors are to be applied to  groups  of  multicore  cables  for  which  the  current-carrying  capacity  for  a single circuit is obtained from Columns 2 and  3  of  Tables  9,  10,  12  and  13,  Column 2  of  Tables 11  and  14,  and  Tables 15 to 19. The factors are also applicable to  groups of  multicore cables making up  parallel circuits in  accordance  with Clause 3.5.2.7.

- These factors are applicable to  uniform groups of  cables, equally loaded. In  accordance with Clause 3.5.6 the factors        for circuits subject to intermittent or varying loads may be higher.

- These factors are  applicable to  single layers of  cables as  shown in  Column 2.  Where there is  more than one  layer on     the same tray or ladder support, Table 22 may be used.

- The vertical spacing of horizontal trays and ladder supports shall be not less than 300 mm.

- The horizontal spacing of vertical trays mounted back-to-back shall be not less than 230 mm.

- No derating factor is applicable for the minimum spacings specified in Clause 3.5.2.2(c) and Figure 1(b).

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

59	AS/NZS 3008.1.2:1998

### TABLE	25(1)

DERATING FACTORS FOR GROUPS OF CIRCUITS OF SINGLE-CORE OR MULTICORE CABLES BURIED DIRECT IN THE   GROUND—

SINGLE-CORE CABLES

| 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| --- | --- | --- | --- | --- | --- | --- |
| Number of circuits |  |  |  |  |  |  |
|  | Derating factors |  |  |  |  |  |
|  | Touching |  | Distance (S), m |  |  |  |
|  |  |  | 0.15 | 0.30 | 0.45 | 0.60 |
|  | Trefoil | Laid flat |  |  |  |  |
| 2 3 4 5 6 7 8 9 10 11 12 | 0.78 0.66 0.61 0.56 0.53 0.50 0.49 0.47 0.46 0.44 0.43 | 0.81 0.70 0.64 0.60 0.57 0.54 0.53 0.51 0.50 0.49 0.48 | 0.83 0.73 0.68 0.64 0.61 0.59 0.57 0.56 0.55 0.54 0.53 | 0.88 0.79 0.74 0.73 0.71 0.69 0.68 0.67 0.67 0.66 0.66 | 0.91 0.84 0.81 0.79 0.78 0.76 0.76 0.75 0.75 0.74 0.74 | 0.93 0.87 0.85 0.83 0.82 0.82 0.81 0.81 0.80 0.80 0.80 |

TABLE	25(2)

DERATING FACTORS FOR GROUPS OF CIRCUITS OF SINGLE-CORE OR MULTICORE CABLES BURIED DIRECT IN THE   GROUND—

MULTICORE CABLES

| 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- |
| Number of cables in group |  |  |  |  |  |
|  | Derating factors |  |  |  |  |
|  | Touching | Distance (S), m |  |  |  |
|  |  | 0.15 | 0.30 | 0.45 | 0.60 |
| 2 | 0.81 | 0.87 | 0.91 | 0.93 | 0.95 |
| 3 | 0.70 | 0.78 | 0.84 | 0.88 | 0.90 |
| 4 | 0.63 | 0.74 | 0.81 | 0.86 | 0.89 |
| 5 | 0.59 | 0.70 | 0.78 | 0.84 | 0.87 |
| 6 | 0.55 | 0.68 | 0.77 | 0.83 | 0.87 |
| 7 | 0.52 | 0.66 | 0.75 | 0.82 | 0.86 |
| 8 | 0.50 | 0.64 | 0.75 | 0.81 | 0.86 |
| 9 | 0.48 | 0.63 | 0.74 | 0.81 | 0.85 |
| 10 | 0.47 | 0.62 | 0.73 | 0.80 | 0.85 |
| 11 | 0.45 | 0.61 | 0.73 | 0.80 | 0.85 |
| 12 | 0.44 | 0.60 | 0.72 | 0.80 | 0.84 |

NOTES:

- For derating factors applicable to  other arrangements of  single-core and multicore cables laid direct in  the ground, refer     to ERA Report 69-30 or alternative   specifications.

- The derating factors have been determined from the hottest cable in  the group and assume that all cables are of  the         same thermal grade of  insulation.

COPYRIGHT

AS/NZS 3008.1.2:1998	60

### TABLE	26(1)

DERATING FACTORS FOR GROUPS OF CIRCUITS OF SINGLE-CORE OR MULTICORE CABLES INSTALLED IN UNDERGROUND WIRING ENCLOSURES— SINGLE CORE CABLES ENCLOSED SEPARATELY

| 1 | 2 | 3 | 4 |
| --- | --- | --- | --- |
| Number of circuits |  |  |  |
|  | Derating factor |  |  |
|  | Touching | Distance (S), m |  |
|  |  | 0.45 | 0.60 |
| 2 | 0.87 | 0.91 | 0.93 |
| 3 | 0.78 | 0.84 | 0.87 |
| 4 | 0.74 | 0.81 | 0.85 |
| 5 | 0.70 | 0.79 | 0.83 |
| 6 | 0.69 | 0.78 | 0.82 |
| 7 | 0.67 | 0.76 | 0.82 |
| 8 | 0.66 | 0.76 | 0.81 |
| 9 | 0.65 | 0.75 | 0.81 |
| 10 | 0.64 | 0.75 | 0.80 |
| 11 | 0.63 | 0.74 | 0.80 |
| 12 | 0.63 | 0.74 | 0.80 |

TABLE	26(2)

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

DERATING FACTORS FOR GROUPS OF CIRCUITS OF SINGLE-CORE OR MULTICORE CABLES INSTALLED IN UNDERGROUND WIRING ENCLOSURES— MULTICORE

CABLES ENCLOSED SEPARATELY OR MORE THAN ONE SINGLE-CORE CABLE PER WIRING  ENCLOSURE

| 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- |
| Number of circuits |  |  |  |  |
|  | Derating factor |  |  |  |
|  | Touching | Distance (S), m |  |  |
|  |  | 0.30 | 0.45 | 0.60 |
| 2 | 0.90 | 0.93 | 0.95 | 0.96 |
| 3 | 0.83 | 0.88 | 0.91 | 0.93 |
| 4 | 0.79 | 0.85 | 0.89 | 0.92 |
| 5 | 0.75 | 0.83 | 0.88 | 0.91 |
| 6 | 0.73 | 0.82 | 0.87 | 0.90 |
| 7 | 0.71 | 0.81 | 0.86 | 0.89 |
| 8 | 0.70 | 0.80 | 0.85 | 0.89 |
| 9 | 0.68 | 0.79 | 0.85 | 0.89 |
| 10 | 0.67 | 0.79 | 0.85 | 0.89 |
| 11 | 0.66 | 0.78 | 0.84 | 0.88 |
| 12 | 0.66 | 0.78 | 0.84 | 0.88 |

NOTE: For derating factors applicable to  other  arrangements  of  cables  in  underground  wiring  enclosures, refer to ERA Report 69-30 or alternative   specifications.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

61	AS/NZS 3008.1.2:1998

### TABLE	27(1)

RATING FACTORS FOR VARIATIONS IN AMBIENT TEMPERATURE FOR CABLES IN AIR OR HEATED CONCRETE SLABS AND FOR CABLES BURIED DIRECT IN GROUND OR IN UNDERGROUND WIRING  ENCLOSURES— AIR

AND CONCRETE SLAB  TEMPERATURES

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor tempera- ture °C | Rating factor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Ambient temperature (See Notes 1, 2 & 3), °C |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 100 | 110 | 120 | 130 | 140 |
| 150 | 1.07 | 1.05 | 1.03 | 1.00 | 0.98 | 0.96 | 0.94 | 0.91 | 0.89 | 0.87 | 0.85 | 0.82 | 0.80 | 0.77 | 0.74 | 0.71 | 0.66 | 0.58 | 0.50 | 0.41 | 0.29 |
| 110 | 1.08 | 1.06 | 1.03 | 1.00 | 0.97 | 0.93 | 0.90 | 0.87 | 0.83 | 0.79 | 0.75 | 0.71 | 0.66 | 0.61 | 0.56 | 0.50 | 0.36 | — | — | — | — |
| 90 | 1.15 | 1.09 | 1.05 | 1.00 | 0.95 | 0.91 | 0.85 | 0.80 | 0.74 | 0.66 | 0.59 | 0.52 | 0.43 | 0.31 | 0.17 | — | — | — | — | — | — |
| 80 | 1.17 | 1.12 | 1.06 | 1.00 | 0.95 | 0.89 | 0.82 | 0.75 | 0.68 | 0.59 | 0.50 | 0.40 | 0.24 | — | — | — | — | — | — | — | — |
| 75 | 1.18 | 1.12 | 1.06 | 1.00 | 0.94 | 0.88 | 0.80 | 0.72 | 0.63 | 0.53 | 0.43 | 0.32 | — | — | — | — | — | — | — | — | — |

NOTES:

- For heated concrete slabs, the ambient temperature shall be taken as the operating temperature of the slab.

- The normal usage of high temperature insulant cables is in ambient air temperatures greater than 30°C, see Table 17.

- For cables with a maximum permissible operating temperature above the normal use temperatures specified in Table 2, derating may not be necessary (see Notes to Table 1 for further details).

### TABLE	27(2)

RATING FACTORS FOR VARIATIONS IN AMBIENT TEMPERATURE FOR CABLES IN AIR OR HEATED CONCRETE SLABS AND    FOR

CABLES BURIED DIRECT IN GROUND OR IN UNDERGROUND WIRING ENCLOSURES— SOIL TEMPERATURES

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor temperature °C | Rating factor |  |  |  |  |  |  |
|  | Soil ambient temperature, °C |  |  |  |  |  |  |
|  | 10 | 15 | 20 | 25 | 30 | 35 | 40 |
| 110 | 1.02 | 1.00 | 0.97 | 0.94 | 0.92 | 0.89 | 0.86 |
| 90 | 1.04 | 1.00 | 0.96 | 0.93 | 0.91 | 0.87 | 0.83 |
| 80 | 1.04 | 1.00 | 0.95 | 0.92 | 0.88 | 0.83 | 0.78 |
| 75 | 1.04 | 1.00 | 0.95 | 0.91 | 0.86 | 0.81 | 0.75 |

COPYRIGHT

AS/NZS 3008.1.2:1998	62

### TABLE	28(1)

RATING FACTORS FOR VARIATIONS IN DEPTH OF LAYING FOR CABLES BURIED DIRECT IN THE GROUND AND FOR   CABLES

INSTALLED IN UNDERGROUND WIRING ENCLOSURES— SINGLE-CORE OR MULTICORE CABLES BURIED  DIRECT

| 1 | 2 | 3 | 4 |
| --- | --- | --- | --- |
| Depth of laying m | Rating factor |  |  |
|  | Conductor size, mm2 |  |  |
|  | Up to 50 | Above 50 up to 300 | Above 300 |
| 0.5 | 1.00 | 1.00 | 1.00 |
| 0.6 | 0.99 | 0.98 | 0.97 |
| 0.8 | 0.97 | 0.96 | 0.94 |
| 1.0 | 0.95 | 0.94 | 0.92 |
| 1.25 | 0.94 | 0.92 | 0.90 |
| 1.5 | 0.93 | 0.91 | 0.89 |
| 1.75 | 0.92 | 0.89 | 0.87 |
| 2.0 | 0.91 | 0.88 | 0.86 |
| 2.5 | 0.90 | 0.87 | 0.85 |
| 3.0 or more | 0.89 | 0.86 | 0.83 |

NOTE: The ambient temperature at the surface is to be taken at  30°C and  not 15°C as  at  a  depth of 0.5 m. For depth less than 0.5 m, see Table 2.3.

### TABLE	28(2)

RATING FACTORS FOR VARIATIONS IN DEPTH   OF

LAYING FOR CABLES BURIED DIRECT IN THE GROUND AND FOR CABLES INSTALLED IN  UNDERGROUND

WIRING ENCLOSURES— SINGLE-CORE AND MULTICORE CABLES IN UNDERGROUND WIRING  ENCLOSURES

| 1 | 2 | 3 |
| --- | --- | --- |
| Depth of laying m | Rating factor |  |
|  | Single-core* | Multicore |
| 0.5 | 1.00 | 1.00 |
| 0.6 | 0.98 | 0.99 |
| 0.8 | 0.95 | 0.97 |
| 1.0 | 0.93 | 0.96 |
| 1.25 | 0.90 | 0.95 |
| 1.5 | 0.89 | 0.94 |
| 1.75 | 0.88 | 0.94 |
| 2.0 | 0.87 | 0.93 |
| 2.5 | 0.86 | 0.93 |
| 3.0 or more | 0.85 | 0.92 |

* These rating factors apply to  single-core cables enclosed separately, or grouped in a single wiring   enclosure.

NOTE: The ambient temperature at  the surface is  to  be  taken as  30°C and not  15°C as at a depth of 0.5 m. For depth less than 0.5 m, see Table 2.4.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

63	AS/NZS 3008.1.2:1998

### TABLE	29

RATING FACTORS FOR CABLES BURIED DIRECT IN GROUND AND FOR CABLES INSTALLED IN UNDERGROUND WIRING ENCLOSURES WHERE THE THERMAL RESISTIVITY OF THE SOIL   VARIES

FROM 1.2°C.m/W

| 1 | 2 | 3 | 4 | 5 | 6 |
| --- | --- | --- | --- | --- | --- |
| Thermal resistivity of soil °C.m/W | Rating factor |  |  |  |  |
|  | Multicore cable buried direct | Two or three single-core cables buried direct | Multicore cable in a wiring enclosure | Two single- core cables in a wiring enclosure* | Three single- core cables in a wiring enclosure* |
| 0.8 | 1.09 | 1.16 | 1.03 | 1.06 | 1.08 |
| 0.9 | 1.07 | 1.11 | 1.02 | 1.04 | 1.06 |
| 1.0 | 1.04 | 1.07 | 1.02 | 1.03 | 1.04 |
| 1.2 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| 1.5 | 0.92 | 0.90 | 0.95 | 0.94 | 0.92 |
| 2.0 | 0.81 | 0.80 | 0.88 | 0.86 | 0.83 |
| 2.5 | 0.74 | 0.72 | 0.83 | 0.80 | 0.77 |
| 3.0 | 0.69 | 0.66 | 0.78 | 0.75 | 0.71 |

* These rating factors apply to single-core cables enclosed separately, or grouped in a single wiring enclosure.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	64

## S  E  C  T  I O N	4	V  O  L  T  A G E	D  R  O P

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

GENERAL The provisions of this Section apply to the selection of conductor sizes with regard to voltage  drop.

NOTE: NZS 3000 imposes limitations on circuit arrangements in order to restrict excessive  voltage drop between supply and  load.

Clauses 4.2 and 4.3 describe a simplified method of determining the voltage drop for use with Tables 40 to 50 for applications where only the route length and load current of balanced circuits are  known.

Clauses 4.4 and 4.5 describe a  more accurate method of determining the voltage drop for  use with Tables 30 to 39 where the cable size is known or anticipated.

Clause 4.6 describes a method for determining the voltage drop where unbalanced load current conditions occur.

  - DETERMINATION OF VOLTAGE DROP FROM  MILLIVOLTS  PER AMPERE METRE The voltage drop (mV/A.m) values given in Tables 40 to 50 are for various cable types and configurations and maximum operating   temperatures.

In applying these voltage drop values, the smallest permissible conductor is the smallest which satisfies the following  equations:

. . . 4.2(1)

. . . 4.2(2)

Vp  sum of Vd on circuit run where

Vc = the millivolt drop per ampere-metre route length of circuit, as shown  in  the  tables for various conductors, in millivolts per ampere metre    (mV/A.m)

NOTE: To convert single-phase voltage drop (mV/A.m) values to three-phase  values,  multiply the single-phase values by 0.866. To convert three-phase values to single-phase values, multiply the three-phase values by   1.155.

Vd  =  actual voltage drop, in  volts

Vp = permissible voltage drop on the circuit  run,  e.g.  5 %  of  supply  voltage,  in  volts

L    =  route length of circuit, in   metres

I     =  the current to be carried by the cable, in    amperes.

The voltage drop values in Tables 40 to 50 may not be applicable under the following conditions:

- Where the cable operating temperature is lower than the maximum temperature permitted for the insulant material. See Clause 4.4 for a method of determining the cable operating temperature for use with the   tables.

- Where the load power factor and cable power factor do not give rise to  conditions    for maximum voltage drop, or the load power factor for  larger  size  conductors  varies from 0.8 lagging. See Clause 4.5 for a  method of determining the voltage    drop where other power factor values are known to be consistent.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

65	AS/NZS 3008.1.2:1998

- Where out-of-balance load conditions exist. See Clause 4.6 for a method of determining the actual voltage drop on a circuit where out-of-balance loads  are  known to be  consistent.

### DETERMINATION OF VOLTAGE DROP FROM CIRCUIT   IMPEDANCE

    - General Voltage drop in a circuit represents the vectorial difference in voltage between the origin or supply end and the load end. For the purpose of determining the maximum voltage drop value in Clause 4.2, the voltage drop (Vd) has been related to the impedance of the cables forming the circuit when the power factor of the cable is equal to  the power factor of the load, in which   case—

Vd  = IZc	. . . 4.3(1)

where

Vd  =  voltage drop in cable, in  volts

I	=  current flowing in cable, in  amperes

Zc  =  impedance of cable, in  ohms

=  (R2c + X2c)

where

Rc  =  cable resistance, in  ohms; a  function of  the material, size and temperature of  the conductors

Xc  = cable reactance, in ohms; a function of the conductor shape and cable spacing

=  0, for direct current  conditions.

The impedance of cables is usually expressed in units of ohms per metre or ohms per kilometre, which enables the total impedance for any given cable length to be readily calculated. In voltage drop applications it is not uncommon for the unit to be expressed as volts per ampere metre which, because of the physical size of the unit with relation to  commonly used cable sizes,  is expressed  in this  Standard  as millivolts  per  ampere metre (mV/A.m).

Therefore the actual volt drop in a cable is obtained by multiplying the cable impedance value by the length of cable and the current as follows:

. . . 4.3(2)

In circuit applications more than one cable is involved and the term  (L)  is  generally  defined as the route length of the circuit. (See    Clause 1.4.4.)

    - Single-phase, two-wire supply system   For a  single-phase circuit the impedance    of the active and neutral conductors are taken into account. As these conductors are of the same material and generally the same size, the voltage drop on the circuit is twice what it would be for a single  cable—

. . . 4.3(3)

or

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	66

    - Three-phase, three-wire or four-wire supply system For a balanced three-phase circuit no current is flowing in the neutral conductor and at any given instant the current flowing in one active conductor will be balanced by the  currents  flowing  in  the  other active conductors. The voltage drop per phase to neutral is the voltage drop in  one cable  and the voltage drop between phases is   therefore—

. . . 4.3(4)

or

As the single-phase voltage drop (mV/A.m) values represent 2Zc and the  three-phase  voltage drop (mV/A.m) values represent 3Zc, then the following  conversions  may  be  used:

- Single-phase voltage drop (mV/A.m) value = 1.155 × three-phase voltage drop (mV/A.m) value.

- Three-phase voltage drop (mV/A.m) value = 0.866 × single-phase voltage drop (mV/A.m) value.

    - Two-phase, three-wire, earthed neutral 120-degree supply  system  For  a balanced two-phase circuit of this type the current flowing in the neutral conductor will balance the currents flowing in the active conductors. The voltage drop may be assessed     on a  single-phase basis by summing the voltage drop in one active conductor (IZc) with     the in-phase component of voltage drop in the neutral (0.5IZc), i.e.

. . . 4.3(5)

    - Single-phase, three-wire, earthed centre-tapped 180-degree supply system   For  a balanced single-phase circuit of this type no current is flowing in the neutral or centre-tapped conductor. Therefore the voltage drop on a single-phase basis will  only be  that associated with the current flowing in    one active conductor, i.e.

. . . 4.3(6)

  - DETERMINATION OF VOLTAGE DROP FROM CABLE OPERATING TEMPERATURE As described in Clause 3.2.2 and Table 1  of  this  Standard,  the sustained cable current-carrying capacities given in Tables 3 to 19 are based on cables operating at the maximum conductor temperature permitted by the  cable  insulation material when installed in specified ambient conditions. In many situations, however, the cable operating temperature is considerably  less  than  the  maximum  figure.  Some situations where this will occur are as   follows:

- Cables sizes are selected in order not to exceed a certain voltage drop figure.

- Cable sizes are selected for convenience, mechanical strength or short-circuit  capacity as required by NZS  3000.

COPYRIGHT

67	AS/NZS 3008.1.2:1998

- The ambient air or soil temperatures are consistently below the specified or standard conditions.

An accurate calculation of conductor temperature can be made using  the  following equation:

. . . 4.4(1)

where

I0   =  operating current, in  amperes

IR   =     rated current given in Tables 3 to 21, in amperes

0  =      operating temperature of cable when carrying I0, in degrees Celsius

R = rated or maximum operating temperature determined  from  Table  1  when carrying IR, in degrees  Celsius

A  =  ambient air or soil temperature, in degrees   Celsius

= under rated conditions— 30°C for air

15°C for ground

(For different ambient temperatures it will be necessary to correct IR by means of factors given in Table  27.)

The calculated operating temperature (0) is then raised to the nearest temperature 45°C, 60°C, 75°C, 80°C, 90°C or 110°C for use with Tables 34 to 50 to determine the cable a.c. resistance and three-phase voltage  drop.

  - DETERMINATION OF VOLTAGE DROP FROM LOAD  POWER  FACTOR  The relationship between the supply and load voltages under different conditions of load power factor is illustrated in the phasor diagrams of    Figure 2.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

From the phasor diagrams of  Figure 2  it can be seen that a  larger value of  supply voltage  is required to maintain a given load voltage when the current is lagging the voltage than when the same current and voltage are in phase. Furthermore,  a  still  smaller  supply voltage is required to maintain the given load voltage when the current leads the load voltage.

The voltage drop (IZc) is the same in all cases, but because of the different power factors   the voltage (IZc) is added to the load voltage at a  different angle in each case. It can be    seen that in the particular instance where the cable power factor and the load power factor are equal, the voltage drop (Vd) is a maximum of IZc as discussed in Clause 4.3.

In other situations of load power factor the difference between the  magnitudes  of  the  supply voltage (E) and the load voltage (VL) is smaller. It will be noted that the magnitude   of the phasors IRc and IXc has been exaggerated with respect to VL in Figure 2 to illustrate   the point. In practice the voltage drop is very much smaller than the supply voltage and

| the difference between the magnitudes of the supply approximated by the following equation: | and | load | voltages may be |
| --- | --- | --- | --- |
| E − VL = I(Rc cos  + Xc sin ) for lagging p.f. |  |  | . . . 4.5(2) |
| = I(Rc cos  − Xc sin ) for leading p.f. |  |  | . . . 4.5(3) |

Therefore for a single-phase  system:

Vd1	=  IL [2(Rc cos  +   Xc sin )]	. . . 4.5(4) and for a three-phase  system:

Vd3	=  IL [   3(Rc cos  + Xc    sin )]	. . . 4.5(5)

COPYRIGHT

AS/NZS 3008.1.2:1998	68

where

L	=  route length of circuit, in  metres

Rc	=  cable resistance, in ohms per  metre

Xc	=  cable reactance, in ohms per  metre.

Values of Rc and Xc are given in units of ohms per kilometre (/km) in Tables 30 to 39. It  will be noted that the influence of skin effect on resistance has been taken into account in  the specification of cable resistance values in Tables 34 to 39 and as such are referred to     as values of a.c.  resistance.

FIGURE  2	PHASOR DIAGRAMS ILLUSTRATING VOLTAGE DROP VARIATION WITH LOAD POWER FACTOR FOR SINGLE  CABLE

  - DETERMINATION OF VOLTAGE DROP IN UNBALANCED MULTIPHASE CIRCUITS For unbalanced multiphase circuits, current will be flowing in the neutral conductor as illustrated in the phasor diagram of Figure    3.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

69	AS/NZS 3008.1.2:1998

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

FIGURE  3	PHASOR DIAGRAM OF CURRENTS IN UNBALANCED THREE-PHASE CIRCUIT

A conservative solution to the voltage drop assessment in these situations would be to assume balanced three-phase load conditions and perform calculations using the current flowing in the heaviest-loaded phase. In many cases this will still be necessary if the out-of-balance conditions are inconsistent or  intermittent.

However, where the currents in each phase can be shown to be of different magnitudes for consistent periods, voltage drop calculations can be performed on a single-phase basis by geometrically summing the voltage drop in the heaviest loaded phase and the voltage drop   in the neutral, as  follows:

Vd  =  voltage drop in heaviest loaded active + voltage drop in    neutral

=  IALAZcA + INLNZcN	. . . 4.6(1)

The voltage drop in each conductor can then be assessed with a knowledge of the specific conductor material, size, temperature and length, the magnitude and phase angle of the current flowing in each conductor, and the phase angle of the  load  by using  the appropriate equations given in this  Clause.

COPYRIGHT

AS/NZS 3008.1.2:1998	70

### TABLE	30

REACTANCE AT 50 Hz OF ALL CABLES EXCLUDING FLEXIBLE CORDS AND CABLES, MINERAL-INSULATED METAL-SHEATHED  CABLES

AND AERIAL CONDUCTORS

| Conduc- tor size mm2 | Reactance at 50 Hz, /km |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Single-core |  |  |  |  |  | Multicore |  |  |  |  |
|  | Trefoil (or single phase) |  |  | Flat touching* |  |  | Circular conductors |  |  | Shaped conductors |  |
|  | Elastomer | PVC | XLPE | Elastomer | PVC | XLPE | Elastomer | PVC | XLPE | PVC | XLPE |
| 1.0 | 0.179 | 0.168 | 0.166 | 0.194 | 0.184 | 0.181 | 0.139 | 0.119 | 0.114 | — | — |
| 1.5 | 0.167 | 0.157 | 0.155 | 0.183 | 0.172 | 0.170 | 0.129 | 0.111 | 0.107 | — | — |
| 2.5 | 0.153 | 0.143 | 0.141 | 0.168 | 0.159 | 0.156 | 0.118 | 0.102 | 0.0988 | — | — |
| 4 | 0.142 | 0.137 | 0.131 | 0.157 | 0.152 | 0.146 | 0.110 | 0.102 | 0.0930 | — | — |
| 6 | 0.133 | 0.128 | 0.123 | 0.148 | 0.143 | 0.138 | 0.104 | 0.0967 | 0.0887 | — | — |
| 10 | 0.123 | 0.118 | 0.114 | 0.138 | 0.134 | 0.129 | 0.0967 | 0.0906 | 0.0840 | — | — |
| 16 | 0.114 | 0.111 | 0.106 | 0.130 | 0.126 | 0.122 | 0.0913 | 0.0861 | 0.0805 | 0.0794 | 0.0742 |
| 25 | 0.109 | 0.106 | 0.102 | 0.125 | 0.121 | 0.118 | 0.0895 | 0.0853 | 0.0808 | 0.0786 | 0.0744 |
| 35 | 0.104 | 0.101 | 0.0982 | 0.120 | 0.117 | 0.113 | 0.0863 | 0.0826 | 0.0786 | 0.0761 | 0.0725 |
| 50 | 0.0988 | 0.0962 | 0.0924 | 0.114 | 0.111 | 0.108 | 0.0829 | 0.0797 | 0.0751 | 0.0734 | 0.0692 |
| 70 | 0.0941 | 0.0917 | 0.0893 | 0.109 | 0.107 | 0.104 | 0.0798 | 0.0770 | 0.0741 | 0.0710 | 0.0683 |
| 95 | 0.0924 | 0.0904 | 0.0868 | 0.108 | 0.106 | 0.102 | 0.0790 | 0.0766 | 0.0725 | 0.0706 | 0.0668 |
| 120 | 0.0889 | 0.0870 | 0.0844 | 0.104 | 0.102 | 0.0996 | 0.0765 | 0.0743 | 0.0713 | 0.0685 | 0.0657 |
| 150 | 0.0885 | 0.0868 | 0.0844 | 0.104 | 0.102 | 0.0996 | 0.0765 | 0.0745 | 0.0718 | 0.0687 | 0.0662 |
| 185 | 0.0878 | 0.0862 | 0.0835 | 0.103 | 0.101 | 0.0988 | 0.0762 | 0.0744 | 0.0720 | 0.0686 | 0.0663 |
| 240 | 0.0861 | 0.0847 | 0.0818 | 0.101 | 0.0999 | 0.0970 | 0.0751 | 0.0735 | 0.0709 | 0.0678 | 0.0653 |
| 300 | 0.0852 | 0.0839 | 0.0809 | 0.100 | 0.0991 | 0.0961 | 0.0746 | 0.0732 | 0.0704 | 0.0675 | 0.0649 |
| 400 | 0.0841 | 0.0829 | 0.0802 | 0.0993 | 0.0982 | 0.0955 | 0.0740 | 0.0728 | 0.0702 | 0.0671 | 0.0647 |
| 500 | 0.0830 | 0.0820 | 0.0796 | 0.0983 | 0.0973 | 0.0948 | 0.0734 | 0.0723 | 0.0700 | 0.0666 | 0.0645 |
| 630 | 0.0809 | 0.0800 | 0.0787 | 0.0961 | 0.0952 | 0.0940 | — | — | — | — | — |

- These reactance values may also be used as  a  conservative  estimate  for  cables  which  are  not  strictly  arranged  ‘flat  touching’,  e.g. where cables are installed in a wiring   enclosure.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

71	AS/NZS 3008.1.2:1998

### TABLE	31

REACTANCE AT 50 Hz OF FLEXIBLE CORDS AND   CABLES

| Conductor size mm2 | Reactance at 50 Hz, /km |  |  |  |
| --- | --- | --- | --- | --- |
|  | Single-core |  | Multicore |  |
|  | Trefoil (or single phase) | Flat touching |  |  |
|  | Elastomer and PVC |  | Elastomer | PVC |
| 0.5 | 0.133 | 0.148 | — | 0.115 |
| 0.75 | 0.166 | 0.181 | 0.130 | 0.130 |
| 1.0 | 0.159 | 0.174 | 0.124 | 0.124 |
| 1.5 | 0.151 | 0.167 | 0.118 | 0.118 |
| 2.5 | 0.141 | 0.156 | 0.112 | 0.112 |
| 4 | 0.134 | 0.149 | 0.108 | 0.108 |
| 6 | 0.135 | 0.151 | 0.104 | 0.104 |
| 10 | 0.127 | 0.142 | 0.102 | 0.0982 |
| 16 | 0.118 | 0.134 | 0.0970 | 0.0937 |
| 25 | 0.110 | 0.125 | 0.0921 | 0.0895 |
| 35 | 0.103 | 0.116 | 0.0895 | — |
| 50 | 0.102 | 0.117 | 0.0893 | — |
| 70 | 0.0964 | 0.112 | 0.0859 | — |
| 95 | 0.0957 | 0.111 | 0.0855 | — |
| 120 | 0.0929 | 0.106 | 0.0836 | — |
| 150 | 0.0921 | 0.107 | 0.0833 | — |
| 185 | 0.0920 | 0.107 | 0.0837 | — |
| 240 | 0.0897 | 0.105 | 0.0829 | — |
| 300 | 0.0883 | 0.104 | 0.0823 | — |
| 400 | 0.0864 | 0.102 | 0.0815 | — |
| 500 | 0.0857 | 0.101 | 0.0812 | — |

COPYRIGHT

AS/NZS 3008.1.2:1998	72

### TABLE	32

REACTANCE AT 50 Hz OF  MINERAL-

INSULATED METAL-SHEATHED CABLES

| Conductor size mm2 | Reactance at 50 Hz, /km |  |
| --- | --- | --- |
|  | Single-core (trefoil formation) | Multicore |
| 0.6/0.6 kV cables |  |  |
| 1 | 0.123 | 0.0912 |
| 1.5 | 0.116 | 0.0865 |
| 2.5 | 0.107 | 0.0814 |
| 4 | 0.101 | — |
| 1/1 kV cables |  |  |
| 1.5 | 0.139 | 0.1010 |
| 2.5 | 0.128 | 0.0937 |
| 4 | 0.120 | 0.0879 |
| 6 | 0.112 | 0.0835 |
| 10 | 0.104 | 0.0788 |
| 16 | 0.0976 | 0.0752 |
| 25 | 0.0927 | 0.0723 |
| 35 | 0.0889 | — |
| 50 | 0.0854 | — |
| 70 | 0.0827 | — |
| 95 | 0.0804 | — |
| 120 | 0.0785 | — |
| 150 | 0.0772 | — |
| 185 | 0.0784 | — |
| 240 | 0.0768 | — |
| 300 | 0.0777 | — |
| 400 | 0.0784 | — |

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

73	AS/NZS 3008.1.2:1998

### TABLE	33

REACTANCE AT 50 Hz OF SINGLE-CORE AERIAL CONDUCTORS WITH BARE OR  INSULATED

CONDUCTORS

| Conductor size, mm2, or stranding (No./mm) | Reactance of 50 Hz, /km* |  |
| --- | --- | --- |
|  | Single phase and trefoil | Three cores in flat formation |
| 7/1.00 | 0.371 | 0.386 |
| 6 | 0.369 | 0.383 |
| 7/1.25 | 0.357 | 0.372 |
| 10 | 0.352 | 0.367 |
| 16 | 0.338 | 0.352 |
| 7/1.75 | 0.336 | 0.351 |
| 7/2.00 | 0.328 | 0.342 |
| 25 | 0.323 | 0.338 |
| 35 | 0.313 | 0.328 |
| 7/2.50 | 0.314 | 0.328 |
| 7/2.75 | 0.308 | 0.322 |
| 50 | 0.300 | 0.315 |
| 19/1.75 | 0.301 | 0.316 |
| 7/3.00 | 0.302 | 0.317 |
| 19/2.00 | 0.293 | 0.307 |
| 70 | 0.288 | 0.303 |
| 7/3.50 | 0.292 | 0.307 |
| 7/3.75 | 0.288 | 0.303 |
| 95 | 0.278 | 0.293 |
| 37/1.75 | 0.279 | 0.294 |
| 7/4.50 | 0.277 | 0.291 |
| 19/2.75 | 0.273 | 0.287 |
| 120 | 0.270 | 0.284 |
| 7/4.75 | 0.273 | 0.288 |
| 19/3.00 | 0.267 | 0.282 |
| 150 | 0.263 | 0.278 |
| 19/3.25 | 0.262 | 0.277 |
| 185 | 0.256 | 0.271 |
| 19/3.50 | 0.258 | 0.272 |
| 37/2.50 | 0.257 | 0.271 |

*   Values are based on a spacing of 0.4    m.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

AS/NZS 3008.1.2:1998	74

### TABLE	34

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

a.c. RESISTANCE AT 50 Hz OF SINGLE-CORE   CABLES

| Conductor size mm2 | a.c. resistance at 50 Hz, /km |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Copper* |  |  |  |  | Aluminium |  |  |  |
|  | Conductor temperature, °C |  |  |  |  | Conductor temperature, °C |  |  |  |
|  | 45 | 60 | 75 | 90 | 110 | 45 | 60 | 75 | 90 |
| 1 | 23.3 | 24.5 | 25.8 | 27.0 | 28.7 | — | — | — | — |
| 1.5 | 14.9 | 15.7 | 16.5 | 17.3 | 18.4 | — | — | — | — |
| 2.5 | 8.14 | 8.57 | 9.01 | 9.45 | 10.0 | — | — | — | — |
| 4 | 5.06 | 5.33 | 5.61 | 5.88 | 6.24 | — | — | — | — |
| 6 | 3.38 | 3.56 | 3.75 | 3.93 | 4.17 | — | — | — | — |
| 10 | 2.01 | 2.12 | 2.23 | 2.33 | 2.48 | — | — | — | — |
| 16 | 1.26 | 1.33 | 1.40 | 1.47 | 1.56 | 2.10 | 2.22 | 2.33 | 2.45 |
| 25 | 0.799 | 0.842 | 0.884 | 0.927 | 0.984 | 1.32 | 1.39 | 1.47 | 1.54 |
| 35 | 0.576 | 0.607 | 0.638 | 0.668 | 0.710 | 0.956 | 1.01 | 1.06 | 1.11 |
| 50 | 0.426 | 0.448 | 0.471 | 0.494 | 0.524 | 0.706 | 0.745 | 0.783 | 0.822 |
| 70 | 0.295 | 0.311 | 0.327 | 0.342 | 0.363 | 0.488 | 0.515 | 0.542 | 0.568 |
| 95 | 0.213 | 0.225 | 0.236 | 0.247 | 0.262 | 0.353 | 0.372 | 0.392 | 0.411 |
| 120 | 0.170 | 0.179 | 0.188 | 0.197 | 0.208 | 0.279 | 0.295 | 0.310 | 0.325 |
| 150 | 0.138 | 0.145 | 0.153 | 0.160 | 0.169 | 0.228 | 0.240 | 0.253 | 0.265 |
| 185 | 0.111 | 0.117 | 0.123 | 0.129 | 0.136 | 0.182 | 0.192 | 0.202 | 0.212 |
| 240 | 0.0862 | 0.0905 | 0.0948 | 0.0991 | 0.105 | 0.140 | 0.147 | 0.155 | 0.162 |
| 300 | 0.0703 | 0.0736 | 0.0770 | 0.0803 | 0.0846 | 0.113 | 0.119 | 0.125 | 0.130 |
| 400 | 0.0569 | 0.0595 | 0.0620 | 0.0646 | 0.0677 | 0.0890 | 0.0936 | 0.0981 | 0.103 |
| 500 | 0.0467 | 0.0487 | 0.0506 | 0.0525 | 0.0547 | 0.0709 | 0.0744 | 0.0779 | 0.0813 |
| 630 | 0.0389 | 0.0404 | 0.0418 | 0.0432 | 0.0448 | 0.0571 | 0.0597 | 0.0623 | 0.0649 |

  - For the a.c. resistance of tinned copper conductor, multiply copper value by 1.01.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

75	AS/NZS 3008.1.2:1998

### TABLE	35

a.c. RESISTANCE AT 50 Hz OF MULTICORE CABLES WITH CIRCULAR CONDUCTORS

| Conductor size mm2 | a.c. resistance at 50 Hz, /km |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Copper* |  |  |  |  | Aluminium |  |  |  |  |
|  | Conductor temperature, °C |  |  |  |  | Conductor temperature, °C |  |  |  |  |
|  | 45 | 60 | 75 | 90 | 110 | 45 | 60 | 75 | 80 | 90 |
| 1 | 23.3 | 24.5 | 25.8 | 27.0 | 28.7 | — | — | — | — | — |
| 1.5 | 14.9 | 15.7 | 16.5 | 17.3 | 18.4 | — | — | — | — | — |
| 2.5 | 8.14 | 8.57 | 9.01 | 9.45 | 10.0 | — | — | — | — | — |
| 4 | 5.06 | 5.33 | 5.61 | 5.88 | 6.24 | — | — | — | — | — |
| 6 | 3.38 | 3.56 | 3.75 | 3.93 | 4.17 | — | — | — | — | — |
| 10 | 2.01 | 2.12 | 2.23 | 2.33 | 2.48 | — | — | — | — | — |
| 16 | 1.26 | 1.33 | 1.40 | 1.47 | 1.56 | 2.10 | 2.22 | 2.33 | 2.37 | 2.45 |
| 25 | 0.799 | 0.842 | 0.884 | 0.927 | 0.984 | 1.32 | 1.39 | 1.47 | 1.49 | 1.54 |
| 35 | 0.576 | 0.607 | 0.638 | 0.669 | 0.710 | 0.956 | 1.01 | 1.06 | 1.08 | 1.11 |
| 50 | 0.426 | 0.449 | 0.471 | 0.494 | 0.524 | 0.706 | 0.745 | 0.784 | 0.796 | 0.822 |
| 70 | 0.295 | 0.311 | 0.327 | 0.343 | 0.364 | 0.488 | 0.515 | 0.542 | 0.551 | 0.569 |
| 95 | 0.214 | 0.225 | 0.236 | 0.248 | 0.262 | 0.353 | 0.373 | 0.392 | 0.398 | 0.411 |
| 120 | 0.170 | 0.179 | 0.188 | 0.197 | 0.209 | 0.280 | 0.295 | 0.310 | 0.315 | 0.325 |
| 150 | 0.139 | 0.146 | 0.153 | 0.160 | 0.170 | 0.228 | 0.241 | 0.253 | 0.257 | 0.265 |
| 185 | 0.112 | 0.118 | 0.123 | 0.129 | 0.136 | 0.182 | 0.192 | 0.202 | — | 0.212 |
| 240 | 0.0870 | 0.0912 | 0.0955 | 0.0998 | 0.105 | 0.140 | 0.148 | 0.155 | — | 0.162 |
| 300 | 0.0712 | 0.0745 | 0.0778 | 0.0812 | 0.0852 | 0.113 | 0.119 | 0.125 | — | 0.131 |
| 400 | 0.0580 | 0.0605 | 0.0630 | 0.0656 | 0.0685 | 0.0897 | 0.0943 | 0.0988 | — | 0.103 |
| 500 | 0.0486 | 0.0506 | 0.0525 | 0.0544 | 0.0565 | 0.0730 | 0.0765 | 0.0800 | — | 0.0835 |

  - For the a.c. resistance of tinned copper conductor, multiply copper value by 1.01.

### TABLE	36

a.c. RESISTANCE AT 50 Hz OF MULTICORE CABLES WITH SHAPED CONDUCTORS

| Conductor size mm2 | a.c. resistance at 50 Hz, /km |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Copper* |  |  |  | Aluminium |  |  |  |
|  | Conductor temperature, °C |  |  |  | Conductor temperature, °C |  |  |  |
|  | 45 | 60 | 75 | 90 | 45 | 60 | 75 | 90 |
| 16 | 1.26 | 1.33 | 1.40 | 1.47 | 2.10 | 2.22 | 2.33 | 2.45 |
| 25 | 0.799 | 0.842 | 0.884 | 0.927 | 1.32 | 1.39 | 1.47 | 1.54 |
| 35 | 0.576 | 0.607 | 0.638 | 0.669 | 0.956 | 1.01 | 1.06 | 1.11 |
| 50 | 0.426 | 0.448 | 0.471 | 0.494 | 0.706 | 0.745 | 0.783 | 0.822 |
| 70 | 0.295 | 0.311 | 0.327 | 0.342 | 0.488 | 0.515 | 0.542 | 0.568 |
| 95 | 0.213 | 0.224 | 0.236 | 0.247 | 0.353 | 0.372 | 0.392 | 0.411 |
| 120 | 0.170 | 0.179 | 0.187 | 0.196 | 0.279 | 0.295 | 0.310 | 0.325 |
| 150 | 0.138 | 0.145 | 0.153 | 0.160 | 0.228 | 0.240 | 0.253 | 0.265 |
| 185 | 0.111 | 0.117 | 0.123 | 0.128 | 0.182 | 0.192 | 0.202 | 0.211 |
| 240 | 0.0859 | 0.0902 | 0.0945 | 0.0988 | 0.139 | 0.147 | 0.154 | 0.162 |
| 300 | 0.0698 | 0.0732 | 0.0766 | 0.0800 | 0.112 | 0.118 | 0.124 | 0.130 |
| 400 | 0.0563 | 0.0589 | 0.0615 | 0.0641 | 0.0886 | 0.0932 | 0.0978 | 0.102 |
| 500 | 0.0465 | 0.0485 | 0.0508 | 0.0526 | 0.0716 | 0.0752 | 0.0788 | 0.0824 |

* For the a.c. resistance of tinned copper conductor, multiply copper value by 1.01.

COPYRIGHT

AS/NZS 3008.1.2:1998	76

### TABLE	37

a.c. RESISTANCE AT 50 Hz OF FLEXIBLE CABLES AND CORDS WITH COPPER CONDUCTORS*

| Conductor size mm2 | a.c. resistance at 50 Hz, /km |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Single-core |  |  |  | Multicore |  |  |  |
|  | Conductor temperature, °C |  |  |  | Conductor temperature, °C |  |  |  |
|  | 45 | 60 | 75 | 90 | 45 | 60 | 75 | 90 |
| 0.5 | 42.8 | 45.1 | 47.4 | 49.7 | 42.8 | 45.1 | 47.4 | 49.7 |
| 0.75 | 28.6 | 30.1 | 31.6 | 33.2 | 28.6 | 30.1 | 31.6 | 33.2 |
| 1.0 | 21.4 | 22.6 | 23.7 | 24.9 | 21.4 | 22.6 | 23.7 | 24.9 |
| 1.5 | 14.6 | 15.4 | 16.2 | 17.0 | 14.6 | 15.4 | 16.2 | 17.0 |
| 2.5 | 8.76 | 9.23 | 9.70 | 10.2 | 8.76 | 9.23 | 9.70 | 10.2 |
| 4 | 5.44 | 5.73 | 6.02 | 6.31 | 5.44 | 5.73 | 6.02 | 6.31 |
| 6 | 3.62 | 3.82 | 4.01 | 4.21 | 3.62 | 3.82 | 4.01 | 4.21 |
| 10 | 2.17 | 2.29 | 2.41 | 2.52 | 2.17 | 2.29 | 2.41 | 2.52 |
| 16 | 1.33 | 1.40 | 1.47 | 1.54 | 1.33 | 1.40 | 1.47 | 1.54 |
| 25 | 0.803 | 0.846 | 0.889 | 0.932 | 0.803 | 0.846 | 0.889 | 0.932 |
| 35 | 0.589 | 0.621 | 0.652 | 0.684 | 0.589 | 0.621 | 0.652 | 0.684 |
| 50 | 0.442 | 0.466 | 0.489 | 0.513 | 0.442 | 0.466 | 0.490 | 0.513 |
| 70 | 0.293 | 0.309 | 0.324 | 0.340 | 0.293 | 0.309 | 0.325 | 0.340 |
| 95 | 0.229 | 0.242 | 0.254 | 0.266 | 0.230 | 0.242 | 0.254 | 0.266 |
| 120 | 0.178 | 0.188 | 0.197 | 0.206 | 0.179 | 0.188 | 0.198 | 0.207 |
| 150 | 0.140 | 0.147 | 0.155 | 0.162 | 0.141 | 0.148 | 0.155 | 0.163 |
| 185 | 0.116 | 0.122 | 0.128 | 0.134 | 0.117 | 0.123 | 0.129 | 0.135 |
| 240 | 0.0909 | 0.0955 | 0.100 | 0.105 | 0.0919 | 0.0965 | 0.101 | 0.106 |
| 300 | 0.0729 | 0.0764 | 0.0800 | 0.0836 | 0.0741 | 0.0776 | 0.0811 | 0.0847 |
| 400 | 0.0558 | 0.0583 | 0.0609 | 0.0634 | 0.0573 | 0.0598 | 0.0623 | 0.0648 |
| 500 | 0.0477 | 0.0496 | 0.0518 | 0.0538 | 0.0494 | 0.0514 | 0.0534 | 0.0554 |

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

*       For the a.c. resistance of tinned copper conductors, multiply copper value by 1.01.

### TABLE  38

a.c. RESISTANCE AT 50 Hz OF MINERAL-INSULATED METAL-SHEATHED CABLES

| Conductor size mm2 | a.c. resistance at 50 Hz, /km |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |
|  | 45 | 60 | 75 | 90 | 100 | 105 |
| 1 | 18.9 | 19.9 | 20.9 | 21.9 | 22.6 | 22.9 |
| 1.5 | 12.7 | 13.3 | 14.0 | 14.7 | 15.2 | 15.4 |
| 2.5 | 7.61 | 8.02 | 8.43 | 8.83 | 9.11 | 9.24 |
| 4 | 4.76 | 5.02 | 5.27 | 5.53 | 5.70 | 5.78 |
| 6 | 3.16 | 3.33 | 3.50 | 3.67 | 3.79 | 3.84 |
| 10 | 1.89 | 1.99 | 2.09 | 2.20 | 2.26 | 2.30 |
| 16 | 1.19 | 1.25 | 1.31 | 1.38 | 1.42 | 1.44 |
| 25 | 0.758 | 0.799 | 0.840 | 0.880 | 0.907 | 0.921 |
| 35 | 0.541 | 0.570 | 0.599 | 0.628 | 0.647 | 0.657 |
| 50 | 0.379 | 0.400 | 0.420 | 0.440 | 0.454 | 0.460 |
| 70 | 0.271 | 0.286 | 0.300 | 0.315 | 0.325 | 0.329 |
| 95 | 0.201 | 0.211 | 0.222 | 0.233 | 0.240 | 0.243 |
| 120 | 0.160 | 0.168 | 0.176 | 0.185 | 0.190 | 0.193 |
| 150 | 0.129 | 0.135 | 0.142 | 0.149 | 0.153 | 0.155 |
| 185 | 0.105 | 0.110 | 0.116 | 0.121 | 0.125 | 0.127 |
| 240 | 0.0825 | 0.0866 | 0.0906 | 0.0947 | 0.0975 | 0.0988 |
| 300 | 0.0674 | 0.0706 | 0.0739 | 0.0771 | 0.0792 | 0.0803 |
| 400 | 0.0527 | 0.0550 | 0.0574 | 0.0597 | 0.0613 | 0.0621 |

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

77	AS/NZS 3008.1.2:1998

### TABLE	39

a.c. RESISTANCE AT 50 Hz OF SINGLE-CORE AERIAL CABLES WITH BARE OR INSULATED  CONDUCTORS

| Conductor size, mm2, or stranding (No./mm) | a.c. resistance at 50 Hz, /km* |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Copper |  |  | Aluminium |  |  |  |
|  | Conductor temperature, °C |  |  | Conductor temperature, °C |  |  |  |
|  | 45 | 60 | 75 | 45 | 60 | 75 | 80 |
| 7/1.00 | 3.57 | 3.76 | 3.95 | — | — | — | — |
| 6 | 3.48 | 3.67 | 3.86 | — | — | — | — |
| 7/1.25 | 2.30 | 2.42 | 2.54 | — | — | — | — |
| 10 | 2.07 | 2.18 | 2.29 | — | — | — | — |
| 16 | 1.30 | 1.37 | 1.44 | 2.10 | 2.22 | 2.33 | 2.37 |
| 7/1.75 | 1.16 | 1.23 | 1.29 | — | — | — | — |
| 7/2.00 | 0.895 | 0.943 | 0.991 | — | — | — | — |
| 25 | 0.822 | 0.867 | 0.911 | 1.32 | 1.39 | 1.47 | 1.49 |
| 35 | 0.593 | 0.625 | 0.657 | 0.956 | 1.01 | 1.06 | 1.08 |
| 7/2.50 | — | — | — | 0.917 | 0.967 | 1.02 | 1.03 |
| 7/2.75 | 0.476 | 0.501 | 0.527 | 0.759 | 0.800 | 0.842 | 0.856 |
| 50 | 0.438 | 0.461 | 0.485 | 0.706 | 0.744 | 0.783 | 0.796 |
| 19/1.75 | 0.434 | 0.457 | 0.481 | — | — | — | — |
| 7/3.00 | — | — | — | 0.637 | 0.672 | 0.707 | 0.719 |
| 19/2.00 | 0.333 | 0.351 | 0.369 | — | — | — | — |
| 70 | 0.303 | 0.320 | 0.336 | 0.488 | 0.515 | 0.541 | 0.550 |
| 7/3.50 | 0.295 | 0.310 | 0.326 | — | — | — | — |
| 7/3.75 | 0.256 | 0.270 | 0.284 | 0.407 | 0.430 | 0.452 | 0.460 |
| 95 | 0.219 | 0.231 | 0.242 | 0.352 | 0.372 | 0.391 | 0.398 |
| 37/1.75 | 0.223 | 0.235 | 0.247 | — | — | — | — |
| 7/4.50 | — | — | — | 0.284 | 0.300 | 0.315 | 0.321 |
| 19/2.75 | 0.176 | 0.186 | 0.195 | — | — | — | — |
| 120 | 0.174 | 0.183 | 0.192 | 0.279 | 0.294 | 0.309 | 0.314 |
| 7/4.75 | — | — | — | 0.256 | 0.270 | 0.284 | 0.288 |
| 19/3.00 | 0.148 | 0.156 | 0.163 | — | — | — | — |
| 150 | 0.141 | 0.148 | 0.156 | 0.227 | 0.240 | 0.252 | 0.256 |
| 19/3.25 | — | — | — | 0.202 | 0.213 | 0.224 | 0.228 |
| 185 | 0.113 | 0.119 | 0.125 | 0.181 | 0.191 | 0.201 | 0.204 |
| 19/3.50 | — | — | — | 0.173 | 0.183 | 0.192 | 0.195 |
| 37/2.50 | 0.110 | 0.116 | 0.122 | — | — | — | — |

*  Values are based on a spacing of 0.4    m.

COPYRIGHT

AS/NZS 3008.1.2:1998	78

### TABLE	40

THREE-PHASE VOLTAGE DROP AT 50 Hz OF SINGLE-CORE INSULATED AND SHEATHED COPPER  CONDUCTORS,

| Conductor size mm2 | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 90 |  | 110 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. |
| 1 | 40.3 | — | 42.5 | — | 44.7 | — | 46.8 | — | 49.7 | — |
| 1.5 | 25.9 | — | 27.3 | — | 28.6 | — | 30.0 | — | 31.9 | — |
| 2.5 | 14.1 | — | 14.9 | — | 15.6 | — | 16.4 | — | 17.4 | — |
| 4 | 8.77 | — | 9.24 | — | 9.71 | — | 10.2 | — | 10.8 | — |
| 6 | 5.86 | — | 6.18 | — | 6.49 | — | 6.81 | — | 7.23 | — |
| 10 | 3.49 | — | 3.67 | — | 3.86 | — | 4.05 | — | 4.30 | — |
| 16 | 2.20 | — | 2.31 | — | 2.43 | — | 2.55 | — | 2.70 | — |
| 25 | 1.40 | — | 1.47 | — | 1.54 | — | 1.62 | — | 1.72 | — |
| 35 | 1.01 | — | 1.07 | — | 1.12 | — | 1.17 | — | 1.24 | — |
| 50 | 0.757 | — | 0.795 | — | 0.834 | — | 0.872 | — | 0.924 | — |
| 70 | 0.537 | — | 0.563 | — | 0.589 | — | 0.615 | — | 0.650 | — |
| 95 | 0.402 | — | 0.420 | — | 0.439 | — | 0.457 | — | 0.481 | — |
| 120 | 0.332 | — | 0.345 | — | 0.359 | — | 0.373 | — | 0.392 | — |
| 150 | 0.284 | — | 0.295 | — | 0.305 | — | 0.316 | — | 0.331 | — |
| 185 | 0.245 | 0.245 | 0.253 | 0.253 | 0.261 | — | 0.269 | — | 0.280 | — |
| 240 | 0.211 | 0.208 | 0.216 | 0.214 | 0.221 | 0.220 | 0.227 | 0.226 | 0.235 | 0.234 |
| 300 | 0.191 | 0.185 | 0.195 | 0.190 | 0.198 | 0.195 | 0.202 | 0.199 | 0.208 | 0.206 |
| 400 | 0.175 | 0.166 | 0.178 | 0.169 | 0.181 | 0.173 | 0.183 | 0.176 | 0.187 | 0.181 |
| 500 | 0.165 | 0.150 | 0.166 | 0.153 | 0.168 | 0.156 | 0.170 | 0.158 | 0.172 | 0.162 |
| 630 | 0.155 | 0.138 | 0.156 | 0.140 | 0.157 | 0.142 | 0.159 | 0.144 | 0.160 | 0.146 |

LAID IN TREFOIL

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

79	AS/NZS 3008.1.2:1998

### TABLE	41

THREE-PHASE VOLTAGE DROP AT 50 Hz OF SINGLE-CORE INSULATED AND SHEATHED COPPER CONDUCTORS, LAID FLAT   TOUCHING

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

OR IN A WIRING  ENCLOSURE

| Conductor size mm2 | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 90 |  | 110 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. |
| 1 | 40.3 | — | 42.5 | — | 44.7 | — | 46.8 | — | 49.7 | — |
| 1.5 | 25.9 | — | 27.3 | — | 28.6 | — | 30.0 | — | 31.9 | — |
| 2.5 | 14.1 | — | 14.9 | — | 15.6 | — | 16.4 | — | 17.4 | — |
| 4 | 8.77 | — | 9.24 | — | 9.71 | — | 10.2 | — | 10.8 | — |
| 6 | 5.86 | — | 6.18 | — | 6.49 | — | 6.81 | — | 7.23 | — |
| 10 | 3.49 | — | 3.68 | — | 3.86 | — | 4.05 | — | 4.30 | — |
| 16 | 2.20 | — | 2.32 | — | 2.43 | — | 2.55 | — | 2.71 | — |
| 25 | 1.40 | — | 1.47 | — | 1.55 | — | 1.62 | — | 1.72 | — |
| 35 | 1.02 | — | 1.07 | — | 1.12 | — | 1.18 | — | 1.25 | — |
| 50 | 0.763 | — | 0.801 | — | 0.840 | — | 0.878 | — | 0.929 | — |
| 70 | 0.545 | — | 0.571 | — | 0.597 | — | 0.623 | — | 0.657 | — |
| 95 | 0.413 | — | 0.431 | — | 0.449 | — | 0.467 | — | 0.491 | — |
| 120 | 0.345 | — | 0.358 | — | 0.371 | — | 0.385 | — | 0.403 | — |
| 150 | 0.299 | 0.299 | 0.309 | — | 0.319 | — | 0.330 | — | 0.344 | — |
| 185 | 0.262 | 0.261 | 0.270 | 0.269 | 0.277 | 0.277 | 0.285 | 0.285 | 0.296 | 0.296 |
| 240 | 0.230 | 0.224 | 0.235 | 0.230 | 0.240 | 0.236 | 0.245 | 0.242 | 0.252 | 0.250 |
| 300 | 0.212 | 0.201 | 0.215 | 0.206 | 0.219 | 0.211 | 0.222 | 0.215 | 0.227 | 0.222 |
| 400 | 0.198 | 0.181 | 0.200 | 0.185 | 0.202 | 0.189 | 0.205 | 0.192 | 0.208 | 0.197 |
| 500 | 0.188 | 0.166 | 0.190 | 0.169 | 0.191 | 0.172 | 0.193 | 0.174 | 0.195 | 0.178 |
| 630 | 0.179 | 0.153 | 0.180 | 0.155 | 0.181 | 0.157 | 0.182 | 0.159 | 0.184 | 0.162 |

COPYRIGHT

AS/NZS 3008.1.2:1998	80

### TABLE	42

| Conductor size mm2 | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 90 |  | 110 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. |
| 1 | 40.3 | — | 42.5 | — | 44.7 | — | 46.8 | — | 49.7 | — |
| 1.5 | 25.9 | — | 27.3 | — | 28.6 | — | 30.0 | — | 31.9 | — |
| 2.5 | 14.1 | — | 14.9 | — | 15.6 | — | 16.4 | — | 17.4 | — |
| 4 | 8.77 | — | 9.24 | — | 9.71 | — | 10.2 | — | 10.8 | — |
| 6 | 5.86 | — | 6.18 | — | 6.49 | — | 6.80 | — | 7.22 | — |
| 10 | 3.49 | — | 3.67 | — | 3.86 | — | 4.05 | — | 4.29 | — |
| 16 | 2.19 | — | 2.31 | — | 2.43 | — | 2.55 | — | 2.70 | — |
| 25 | 1.39 | — | 1.47 | — | 1.54 | — | 1.61 | — | 1.71 | — |
| 35 | 1.01 | — | 1.06 | — | 1.11 | — | 1.17 | — | 1.24 | — |
| 50 | 0.751 | — | 0.790 | — | 0.829 | — | 0.868 | — | 0.920 | — |
| 70 | 0.530 | — | 0.556 | — | 0.583 | — | 0.609 | — | 0.645 | — |
| 95 | 0.394 | — | 0.413 | — | 0.431 | — | 0.450 | — | 0.475 | — |
| 120 | 0.323 | — | 0.337 | — | 0.351 | — | 0.366 | — | 0.385 | — |
| 150 | 0.274 | — | 0.285 | — | 0.296 | — | 0.307 | — | 0.322 | — |
| 185 | 0.234 | — | 0.242 | — | 0.251 | — | 0.259 | — | 0.271 | — |
| 240 | 0.198 | 0.198 | 0.204 | 0.204 | 0.210 | 0.210 | 0.216 | 0.216 | 0.224 | — |
| 300 | 0.178 | 0.175 | 0.182 | 0.180 | 0.186 | 0.185 | 0.190 | 0.189 | 0.196 | 0.196 |
| 400 | 0.162 | 0.157 | 0.165 | 0.160 | 0.168 | 0.164 | 0.171 | 0.167 | 0.175 | 0.172 |
| 500 | 0.152 | 0.143 | 0.154 | 0.146 | 0.156 | 0.148 | 0.158 | 0.151 | 0.160 | 0.155 |

THREE-PHASE VOLTAGE DROP AT 50 Hz OF MULTICORE CABLES WITH CIRCULAR COPPER  CONDUCTORS

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

81	AS/NZS 3008.1.2:1998

### TABLE	43

THREE-PHASE VOLTAGE DROP AT 50 Hz OF SINGLE-CORE INSULATED AND SHEATHED ALUMINIUM CONDUCTORS, LAID IN TREFOIL

| Conductor size mm2 | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 90 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f | Max. | 0.8 p.f. | Max. | 0.8 p.f. |
| 16 | 3.65 | — | 3.85 | — | 4.05 | — | 4.25 | — |
| 25 | 2.30 | — | 2.42 | — | 2.55 | — | 2.67 | — |
| 35 | 1.66 | — | 1.75 | — | 1.85 | — | 1.94 | — |
| 50 | 1.23 | — | 1.30 | — | 1.37 | — | 1.43 | — |
| 70 | 0.860 | — | 0.906 | — | 0.952 | — | 0.997 | — |
| 95 | 0.631 | — | 0.663 | — | 0.696 | — | 0.727 | — |
| 120 | 0.507 | — | 0.532 | — | 0.558 | — | 0.582 | — |
| 150 | 0.422 | — | 0.443 | — | 0.463 | — | 0.482 | — |
| 185 | 0.349 | — | 0.364 | — | 0.380 | — | 0.394 | — |
| 240 | 0.283 | — | 0.294 | — | 0.305 | — | 0.314 | — |
| 300 | 0.243 | — | 0.251 | — | 0.260 | — | 0.266 | — |
| 400 | 0.211 | 0.209 | 0.216 | 0.216 | 0.222 | 0.222 | 0.226 | 0.226 |
| 500 | 0.188 | 0.183 | 0.192 | 0.188 | 0.196 | 0.193 | 0.197 | 0.195 |
| 630 | 0.170 | 0.162 | 0.173 | 0.166 | 0.175 | 0.169 | 0.177 | 0.172 |

TABLE	44

THREE-PHASE VOLTAGE DROP AT 50 Hz OF SINGLE-CORE INSULATED AND SHEATHED ALUMINIUM CONDUCTORS, LAID FLAT TOUCHING

| Conductor size mm2 | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 90 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. |
| 16 | 3.65 | — | 3.85 | — | 4.05 | — | 4.25 | — |
| 25 | 2.30 | — | 2.42 | — | 2.55 | — | 2.67 | — |
| 35 | 1.67 | — | 1.76 | — | 1.85 | — | 1.94 | — |
| 50 | 1.24 | — | 1.30 | — | 1.37 | — | 1.44 | — |
| 70 | 0.866 | — | 0.911 | — | 0.956 | — | 1.00 | — |
| 95 | 0.638 | — | 0.670 | — | 0.702 | — | 0.733 | — |
| 120 | 0.515 | — | 0.540 | — | 0.565 | — | 0.589 | — |
| 150 | 0.432 | — | 0.452 | — | 0.472 | — | 0.491 | — |
| 185 | 0.361 | — | 0.376 | — | 0.391 | — | 0.404 | — |
| 240 | 0.297 | — | 0.308 | — | 0.319 | — | 0.327 | — |
| 300 | 0.260 | 0.259 | 0.268 | 0.267 | 0.276 | 0.275 | 0.281 | — |
| 400 | 0.229 | 0.225 | 0.235 | 0.231 | 0.240 | 0.238 | 0.243 | 0.242 |
| 500 | 0.208 | 0.199 | 0.212 | 0.204 | 0.216 | 0.209 | 0.216 | 0.211 |
| 630 | 0.192 | 0.178 | 0.195 | 0.181 | 0.197 | 0.185 | 0.198 | 0.188 |

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	82

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

TABLE	45

THREE-PHASE VOLTAGE DROP AT 50 Hz OF MULTICORE CABLES WITH CIRCULAR ALUMINIUM  CONDUCTORS

| Conductor size mm2 | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 80 |  | 90 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max | 0.8 p.f. | Max. | 0.8 p.f. |
| 16 | 3.64 | — | 3.84 | — | 4.04 | — | 4.11 | — | 4.24 | — |
| 25 | 2.29 | — | 2.42 | — | 2.54 | — | 2.59 | — | 2.67 | — |
| 35 | 1.66 | — | 1.75 | — | 1.84 | — | 1.87 | — | 1.93 | — |
| 50 | 1.23 | — | 1.30 | — | 1.36 | — | 1.39 | — | 1.43 | — |
| 70 | 0.856 | — | 0.902 | — | 0.948 | — | 0.966 | — | 0.993 | — |
| 95 | 0.626 | — | 0.659 | — | 0.691 | — | 0.706 | — | 0.723 | — |
| 120 | 0.501 | — | 0.527 | — | 0.552 | — | 0.565 | — | 0.577 | — |
| 150 | 0.416 | — | 0.436 | — | 0.457 | — | 0.468 | — | 0.476 | — |
| 185 | 0.341 | — | 0.357 | — | 0.373 | — | — | — | 0.388 | — |
| 240 | 0.274 | — | 0.285 | — | 0.297 | — | — | — | 0.307 | — |
| 300 | 0.233 | — | 0.242 | — | 0.251 | — | — | — | 0.258 | — |
| 400 | 0.200 | 0.200 | 0.206 | 0.206 | 0.212 | — | — | — | 0.216 | — |
| 500 | 0.178 | 0.176 | 0.182 | 0.181 | 0.186 | 0.185 | — | — | 0.189 | 0.189 |

NOTE: For aerial bundled cables (ABC) use XLPE single core, trefoil figures.

COPYRIGHT

83	AS/NZS 3008.1.2:1998

### TABLE  46

THREE-PHASE VOLTAGE DROP AT 50 Hz OF SINGLE-CORE FLEXIBLE CABLES AND CORDS WITH COPPER CONDUCTORS, LAID IN   TREFOIL

| Conductor size mm2 | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 90 |  |
|  | Max. | 0.8 p,f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. |
| 0.5 | 74.2 | — | 78.2 | — | 82.2 | — | 86.1 | — |
| 0.75 | 49.5 | — | 52.1 | — | 54.8 | — | 57.4 | — |
| 1.0 | 37.1 | — | 39.1 | — | 41.1 | — | 43.1 | — |
| 1.5 | 25.3 | — | 26.7 | — | 28.0 | — | 29.4 | — |
| 2.5 | 15.2 | — | 16.0 | — | 16.8 | — | 17.6 | — |
| 4 | 9.42 | — | 9.92 | — | 10.4 | — | 10.9 | — |
| 6 | 6.28 | — | 6.62 | — | 6.96 | — | 7.29 | — |
| 10 | 3.77 | — | 3.97 | — | 4.18 | — | 4.38 | — |
| 16 | 2.31 | — | 2.43 | — | 2.56 | — | 2.68 | — |
| 25 | 1.40 | — | 1.48 | — | 1.55 | — | 1.63 | — |
| 35 | 1.04 | — | 1.09 | — | 1.14 | — | 1.20 | — |
| 50 | 0.785 | — | 0.825 | — | 0.866 | — | 0.906 | — |
| 70 | 0.534 | — | 0.560 | — | 0.586 | — | 0.612 | — |
| 95 | 0.431 | — | 0.450 | — | 0.470 | — | 0.490 | — |
| 120 | 0.348 | — | 0.363 | — | 0.377 | — | 0.392 | — |
| 150 | 0.290 | — | 0.301 | — | 0.312 | — | 0.323 | — |
| 185 | 0.257 | 0.257 | 0.265 | 0.265 | 0.273 | 0.273 | 0.282 | 0.282 |
| 240 | 0.221 | 0.219 | 0.227 | 0.226 | 0.233 | 0.232 | 0.239 | 0.238 |
| 300 | 0.196 | 0.193 | 0.202 | 0.198 | 0.206 | 0.203 | 0.211 | 0.208 |
| 400 | 0.178 | 0.167 | 0.181 | 0.171 | 0.183 | 0.174 | 0.186 | 0.178 |
| 500 | 0.170 | 0.155 | 0.172 | 0.158 | 0.173 | 0.161 | 0.175 | 0.164 |

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	84

### TABLE	47

THREE-PHASE VOLTAGE DROP AT 50 Hz OF   MULTICORE

FLEXIBLE CABLES AND CORDS WITH COPPER   CONDUCTORS

| Conductor size mm2 | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 90 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f |
| 0.5 | 74.2 | — | 78.2 | — | 82.2 | — | 86.1 | — |
| 0.75 | 49.5 | — | 52.1 | — | 54.8 | — | 57.4 | — |
| 1.0 | 37.1 | — | 39.1 | — | 41.1 | — | 43.1 | — |
| 1.5 | 25.3 | — | 26.7 | — | 28.0 | — | 29.4 | — |
| 2.5 | 15.2 | — | 16.0 | — | 16.8 | — | 17.6 | — |
| 4 | 9.42 | — | 9.92 | — | 10.4 | — | 10.9 | — |
| 6 | 6.28 | — | 6.62 | — | 6.95 | — | 7.29 | — |
| 10 | 3.77 | — | 3.97 | — | 4.17 | — | 4.38 | — |
| 16 | 2.31 | — | 2.43 | — | 2.55 | — | 2.68 | — |
| 25 | 1.40 | — | 1.47 | — | 1.55 | — | 1.62 | — |
| 35 | 1.03 | — | 1.09 | — | 1.14 | — | 1.19 | — |
| 50 | 0.781 | — | 0.822 | — | 0.862 | — | 0.902 | — |
| 70 | 0.529 | — | 0.555 | — | 0.581 | — | 0.608 | — |
| 95 | 0.425 | — | 0.445 | — | 0.465 | — | 0.485 | — |
| 120 | 0.342 | — | 0.357 | — | 0.371 | — | 0.387 | — |
| 150 | 0.283 | — | 0.294 | — | 0.305 | — | 0.317 | — |
| 185 | 0.249 | 0.249 | 0.258 | 0.258 | 0.266 | 0.266 | 0.275 | 0.274 |
| 240 | 0.214 | 0.214 | 0.220 | 0.220 | 0.226 | 0.226 | 0.233 | 0.233 |
| 300 | 0.192 | 0.188 | 0.196 | 0.193 | 0.200 | 0.198 | 0.205 | 0.203 |
| 400 | 0.173 | 0.164 | 0.175 | 0.168 | 0.178 | 0.171 | 0.180 | 0.174 |
| 500 | 0.165 | 0.153 | 0.166 | 0.156 | 0.168 | 0.158 | 0.170 | 0.161 |

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

85	AS/NZS 3008.1.2:1998

### TABLE	48

THREE-PHASE VOLTAGE DROP AT 50 Hz OF SINGLE-CORE   AND

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

MULTICORE MINERAL-INSULATED METAL-SHEATHED (MIMS) CABLES, LAID IN TREFOIL

| Conductor size mm2 | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 90 |  | 100 |  | 105 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. |
| 0.6/0.6 kV |  |  |  |  |  |  |  |  |  |  |  |  |
| cables |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 | 32.8 | — | 34.6 | — | 36.3 | — | 38.1 | — | 39.1 | 31.4 | 39.7 | 31.9 |
| 1.5 | 21.9 | — | 23.0 | — | 24.2 | — | 25.4 | — | 26.3 | 21.2 | 26.7 | 21.5 |
| 2.5 | 13.1 | — | 13.8 | — | 14.5 | — | 15.2 | — | 15.8 | 12.7 | 16.0 | 12.9 |
| 4 | 8.20 | — | 8.64 | — | 9.08 | — | 9.52 | — | 9.87 | 8.00 | 10.01 | 8.11 |
| 1/1 kV |  |  |  |  |  |  |  |  |  |  |  |  |
| cables |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.5 | 21.9 | — | 23.0 | — | 24.2 | — | 25.4 | — | 26.3 | 21.2 | 26.7 | 21.5 |
| 2.5 | 13.1 | — | 13.8 | — | 14.5 | — | 15.2 | — | 15.8 | 12.8 | 16.0 | 12.9 |
| 4 | 8.20 | — | 8.64 | — | 9.08 | — | 9.52 | — | 9.87 | 8.02 | 10.01 | 8.13 |
| 6 | 5.46 | — | 5.77 | — | 6.05 | — | 6.34 | — | 6.57 | 5.37 | 6.65 | 5.44 |
| 10 | 3.30 | — | 3.47 | — | 3.65 | — | 3.83 | — | 3.92 | 3.24 | 3.99 | 3.30 |
| 16 | 2.06 | — | 2.17 | — | 2.28 | — | 2.39 | — | 2.47 | 2.07 | 2.50 | 2.10 |
| 25 | 1.32 | — | 1.39 | — | 1.46 | — | 1.53 | — | 1.58 | 1.35 | 1.60 | 1.37 |
| 35 | 0.949 | — | 0.999 | — | 1.05 | — | 1.10 | — | 1.13 | 0.99 | 1.15 | 1.00 |
| 50 | 0.672 | — | 0.706 | — | 0.741 | — | 0.775 | — | 0.800 | 0.718 | 0.810 | 0.726 |
| 70 | 0.491 | — | 0.515 | — | 0.539 | — | 0.563 | — | 0.581 | 0.536 | 0.588 | 0.542 |
| 95 | 0.375 | — | 0.393 | — | 0.410 | — | 0.427 | — | 0.438 | 0.416 | 0.443 | 0.420 |
| 120 | 0.307 | — | 0.320 | — | 0.333 | — | 0.346 | — | 0.356 | 0.345 | 0.361 | 0.349 |
| 150 | 0.260 | — | 0.270 | — | 0.280 | — | 0.290 | — | 0.297 | 0.292 | 0.300 | 0.295 |
| 185 | 0.228 | — | 0.236 | — | 0.243 | — | 0.251 | — | 0.256 | 0.255 | 0.258 | 0.257 |
| 240 | 0.195 | 0.194 | 0.201 | 0.200 | 0.206 | 0.206 | 0.211 | 0.211 | 0.215 | 0.215 | 0.217 | 0.217 |
| 300 | 0.178 | 0.173 | 0.181 | 0.178 | 0.185 | 0.182 | 0.189 | 0.187 | 0.192 | 0.190 | 0.194 | 0.192 |
| 400 | 0.163 | 0.154 | 0.166 | 0.157 | 0.168 | 0.161 | 0.170 | 0.164 | 0.172 | 0.166 | 0.173 | 0.168 |

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	86

### TABLE	49

THREE-PHASE VOLTAGE DROP AT 50 Hz OF AERIAL CABLES WITH BARE OR INSULATED COPPER  CONDUCTORS

| Conductor size, mm2, or stranding (No./mm) | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. |
| 7/1.00 | 6.22 | — | 6.55 | — | 6.88 | — |
| 6 | 6.07 | — | 6.39 | — | 6.71 | — |
| 7/1.25 | 4.02 | — | 4.23 | — | 4.45 | — |
| 10 | 3.64 | — | 3.83 | — | 4.02 | — |
| 16 | 2.33 | — | 2.45 | — | 2.56 | — |
| 7/1.75 | 2.10 | — | 2.20 | — | 2.31 | — |
| 7/2.00 | 1.65 | — | 1.73 | — | 1.81 | — |
| 25 | 1.53 | — | 1.60 | — | 1.67 | — |
| 35 | 1.16 | — | 1.21 | — | 1.26 | — |
| 7/2.75 | 0.981 | — | 1.02 | — | 1.06 | — |
| 50 | 0.920 | — | 0.953 | — | 0.988 | — |
| 19/1.75 | 0.915 | — | 0.948 | — | 0.982 | — |
| 19/2.00 | 0.768 | 0.766 | 0.791 | 0.790 | 0.815 | 0.815 |
| 70 | 0.725 | 0.720 | 0.746 | 0.743 | 0.767 | 0.765 |
| 7/3.50 | 0.719 | 0.712 | 0.739 | 0.734 | 0.759 | 0.756 |
| 7/3.75 | 0.668 | 0.654 | 0.684 | 0.673 | 0.700 | 0.692 |
| 95 | 0.613 | 0.592 | 0.626 | 0.609 | 0.639 | 0.625 |
| 37/1.75 | 0.619 | 0.600 | 0.632 | 0.616 | 0.646 | 0.633 |
| 19/2.75 | 0.562 | 0.528 | 0.571 | 0.541 | 0.581 | 0.554 |
| 120 | 0.556 | 0.521 | 0.565 | 0.534 | 0.574 | 0.547 |
| 19/3.00 | 0.529 | 0.482 | 0.536 | 0.493 | 0.543 | 0.504 |
| 150 | 0.517 | 0.469 | 0.524 | 0.479 | 0.530 | 0.490 |
| 185 | 0.485 | 0.423 | 0.489 | 0.431 | 0.494 | 0.439 |
| 37/2.50 | 0.484 | 0.419 | 0.488 | 0.428 | 0.492 | 0.436 |

COPYRIGHT

87	AS/NZS 3008.1.2:1998

### TABLE	50

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

THREE-PHASE VOLTAGE DROP AT 50 Hz OF AERIAL CABLES WITH BARE OR INSULATED ALUMINIUM  CONDUCTORS

| Conductor size, mm2, or stranding (No./mm) | Three-phase voltage drop at 50 Hz, mV/A.m |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductor temperature, °C |  |  |  |  |  |  |  |
|  | 45 |  | 60 |  | 75 |  | 80 |  |
|  | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. | Max. | 0.8 p.f. |
| 16 | 3.69 | — | 3.89 | — | 4.08 | — | 4.15 | — |
| 25 | 2.36 | — | 2.48 | — | 2.60 | — | 2.64 | — |
| 35 | 1.74 | — | 1.83 | — | 1.92 | — | 1.94 | — |
| 7/2.50 | 1.68 | — | 1.76 | — | 1.84 | — | 1.87 | — |
| 7/2.75 | 1.42 | — | 1.48 | — | 1.55 | — | 1.57 | — |
| 50 | 1.33 | — | 1.39 | — | 1.45 | — | 1.47 | — |
| 7/3.00 | 1.22 | — | 1.28 | — | 1.33 | — | 1.34 | — |
| 70 | 0.982 | — | 1.02 | — | 1.06 | — | 1.08 | — |
| 7/3.75 | 0.864 | 0.864 | 0.896 | 0.895 | 0.929 | 0.926 | 0.940 | 0.936 |
| 95 | 0.778 | 0.777 | 0.804 | 0.804 | 0.831 | 0.831 | 0.840 | 0.840 |
| 7/4.50 | 0.687 | 0.681 | 0.707 | 0.703 | 0.727 | 0.725 | 0.734 | 0.732 |
| 120 | 0.672 | 0.667 | 0.691 | 0.688 | 0.711 | 0.709 | 0.718 | 0.716 |
| 7/4.75 | 0.648 | 0.638 | 0.665 | 0.658 | 0.682 | 0.677 | 0.688 | 0.684 |
| 150 | 0.602 | 0.588 | 0.617 | 0.606 | 0.631 | 0.623 | 0.636 | 0.629 |
| 19/3.25 | 0.573 | 0.552 | 0.585 | 0.568 | 0.597 | 0.583 | 0.601 | 0.588 |
| 185 | 0.543 | 0.517 | 0.553 | 0.531 | 0.564 | 0.544 | 0.567 | 0.549 |
| 19/3.50 | 0.538 | 0.508 | 0.547 | 0.521 | 0.557 | 0.534 | 0.560 | 0.538 |

COPYRIGHT

AS/NZS 3008.1.2:1998	88

## S  E  C  T  I O N	5	S H O R T - C I R C U I T P E R F O R M A N C E

  - GENERAL This Section is applicable to the  short-circuit  maximum  temperature rating of electric cables having a rated voltage not  exceeding  0.6/1.0 kV.  Guidance  is  given on the following  aspects:

- Maximum permissible short-circuit temperatures for  cable—

  - insulating materials;

  - outer jacket and bedding materials;  and

  - conductor and metallic sheath materials and   components.

- Influence of the method of installation on the temperature    limit.

- Calculation	of	the	permissible	short-circuit	current	in	the	current-carrying components of the  cable.

  - FACTORS GOVERNING THE APPLICATION OF THE TEMPERATURE LIMITS   The short-circuit temperatures given in  Clause 5.5  are  the actual temperatures  of the current-carrying component as limited by the adjacent materials in the cable and are valid for short-circuit durations of up to 5 s. These temperatures will only be obtained in practice if  non-adiabatic heating is  assumed (that is, an  appropriate allowance for heat   loss into the dielectric during the short circuit is made) when calculating the allowable short-circuit current for a given time (not longer than 5 s). The  use  of  the  adiabatic  method (that is, when heat loss from the current-carrying component  during  the  short  circuit is neglected) gives short-circuit currents that are on  the safe side. The 5-second period quoted is the limit for the temperatures quoted to  be valid, not for the application     of the adiabatic calculation method. The time limit for the use of the adiabatic method has    a different definition, being a function of both the short-circuit duration and the cross-sectional area of the current-carrying  component.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

For thermoplastic insulating materials the limits must be applied with caution when the cables are either directly buried or securely clamped when in air. Local pressure due to clamping or the use of an installation radius less than 8 times the cable outside diameter, especially for cables that are rigidly restrained, can lead to high deforming forces under short-circuit conditions. Where these conditions cannot be avoided it is suggested that the limit be reduced by 10°C. The limits quoted are based on average hardness grades of PVC and some adjustment may be necessary for other grades, especially those compounded for improved low-temperature properties.

NOTES:

- Caution should be exercised when using the limits recommended for thermosetting materials on large conductors because the high mechanical forces combined with any residual characteristics could result in deformation sufficient to cause    failure.

- Caution may be needed with total cross-sectional areas  in  the  region  of  1000  mm2 when using the conductor temperatures specified for impregnated paper, butyl, cross-linked polyethylene (XLPE) and ethylene propylene rubber (EPR) insulation and the cable  is sheathed with a  lower-temperature material.

- Information on the short-circuit performance of MIMS cable is not included in this Standard and reference should be made to manufacturer’s   recommendations.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

89	AS/NZS 3008.1.2:1998

  - CALCULATION OF PERMISSIBLE SHORT-CIRCUIT CURRENTS The following adiabatic method, which neglects heat loss, is accurate enough for calculating permissible conductor and metallic sheath short-circuit currents for the  majority  of practical cases and any error is on the safe side. However, for thin screens the adiabatic method indicates much higher temperature rises than actually occur in practice and thus must be used with some  discretion.

The generalized form of the adiabatic temperature rise equation which is applicable to any starting temperature is as  follows:

I2t = K2S2	. . . 5.3(1)

where

I	=  short-circuit current (r.m.s. over duration), in   amperes

t	=  duration of short circuit, in  seconds

K = constant depending on the material of the  current-carrying  component,  the  initial temperature and the final  temperature

NOTE: Refer to Table 51 for values of constant    (K).

S	=  cross-sectional area of the current-carrying component, in square   millimetres.

NOTE: For conductors and metallic sheaths it is sufficient to take  the  nominal cross-sectional area but in the case of screens, this quantity requires careful consideration.

### TABLE	51

VALUES OF CONSTANT K FOR DETERMINATION OF PERMISSIBLE SHORT-CIRCUIT CURRENTS

Constant (K)

| Initial temp. of conductor °C | Final temperature of conductor, °C |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Copper |  |  |  |  |  | Aluminium |  |  |  | Lead |  | Steel |  |
|  | 140 | 150 | 160 | 220 | 250 | 350 | 140 | 150 | 160 | 250 | 150 | 200 | 150 | 200 |
| 130 | 37.2 | 52.2 | 63.6 | 106 | 121 | 155 | 24.6 | 34.5 | 42.0 | 79.6 | 9.5 | 17.3 | 18.9 | 34.1 |
| 125 | 45.7 | 58.6 | 68.9 | 109 | 123 | 158 | 30.2 | 38.7 | 45.5 | 81.5 | 10.7 | 17.9 | 21.2 | 35.4 |
| 110 | 65.3 | 74.9 | 83.2 | 119 | 132 | 164 | 43.2 | 49.5 | 55.0 | 87.1 | 13.7 | 19.9 | 27.1 | 39.3 |
| 90 | 85.6 | 93.1 | 99.9 | 131 | 143 | 173 | 56.6 | 61.5 | 66.0 | 94.5 | 17.0 | 22.3 | 33.7 | 44.1 |
| 85 | 90.1 | 97.3 | 104 | 134 | 146 | 176 | 59.5 | 64.3 | 68.6 | 96.3 | 17.8 | 22.9 | 35.2 | 45.3 |
| 80 | 94.4 | 101 | 108 | 137 | 149 | 178 | 62.4 | 67.0 | 71.1 | 98.1 | 18.5 | 23.5 | 36.7 | 46.4 |
| 75 | 98.7 | 105 | 111 | 140 | 151 | 180 | 65.2 | 69.6 | 73.6 | 99.9 | 19.2 | 24.0 | 38.2 | 47.6 |
| 70 | 103 | 109 | 115 | 143 | 154 | 182 | 68.0 | 72.2 | 76.0 | 102 | 19.9 | 24.6 | 39.6 | 48.8 |
| 65 | 107 | 113 | 119 | 146 | 157 | 185 | 70.7 | 74.7 | 78.4 | 104 | 20.6 | 25.2 | 41.0 | 49.9 |
| 60 | 111 | 117 | 122 | 149 | 159 | 187 | 73.3 | 77.2 | 80.8 | 105 | 21.3 | 25.7 | 42.4 | 51.0 |
| 55 | 115 | 120 | 126 | 152 | 162 | 189 | 75.8 | 79.6 | 83.1 | 107 | 22.0 | 26.3 | 43.7 | 52.2 |
| 50 | 118 | 124 | 129 | 155 | 165 | 192 | 78.4 | 82.0 | 85.5 | 109 | 22.7 | 26.9 | 45.1 | 53.3 |
| 45 | 122 | 128 | 133 | 158 | 168 | 194 | 80.9 | 84.4 | 87.7 | 111 | 23.3 | 27.4 | 46.4 | 54.4 |
| 40 | 126 | 131 | 136 | 160 | 170 | 196 | 83.3 | 86.8 | 90.0 | 113 | 24.0 | 28.0 | 47.7 | 55.6 |
| 35 | 130 | 135 | 140 | 163 | 173 | 199 | 85.8 | 89.1 | 92.3 | 114 | 24.6 | 28.5 | 49.1 | 56.7 |
| 30 | 133 | 138 | 143 | 166 | 176 | 201 | 88.2 | 91.5 | 94.5 | 116 | 25.3 | 29.1 | 50.4 | 57.8 |
| 25 | 137 | 142 | 146 | 169 | 179 | 204 | 90.6 | 93.8 | 96.8 | 118 | 25.9 | 29.6 | 51.7 | 59.0 |

  - INFLUENCE OF METHOD OF INSTALLATION  When it is intended to make  full use of the short-circuit limits of a cable, consideration should  be  given  to  the  influence of the method of installation. An important aspect concerns  the  extent  and  nature of the mechanical restraint imposed on the cable. Longitudinal expansion of a cable during a short circuit can be significant and when this expansion is restrained the resultant forces are considerable.

COPYRIGHT

AS/NZS 3008.1.2:1998	90

Where cables are installed in air, provision should be made so that expansion may be absorbed uniformly along the length by snaking rather than permitting it to be relieved by excessive movement at a few  points only. Fixings should be  spaced sufficiently far  apart  to permit lateral movement of multi-core cables or groups of single-core cables.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

Where cables are buried directly in the ground, or must be restrained by frequent fixing,  then provision should be made to accommodate the resulting longitudinal forces on terminations and joint boxes. Sharp bends should be avoided because  the  longitudinal  forces are translated into radial pressures at bends in the  cable  route  and  these  may damage thermoplastic components of the cable such as insulation and sheaths. Attention is drawn to  the minimum bending radius recommended for the type of cable. For cables in     air it is also desirable to avoid fixings at a bend which may cause local pressure on  the  cable.

In determining the short-circuit stresses which will be imposed on a  cable,  the characteristics of the protective devices used shall be    considered.

### MAXIMUM PERMISSIBLE SHORT-CIRCUIT  TEMPERATURES

    - General Taking into account the recommendation given in Clause 5.2, the temperature values given in Tables 52 to 54   are—

- the actual temperatures of the current-carrying components;   and

- the limits specified for short-circuits of up to 5 s duration.

    - Insulating materials    The temperature limits given in Table 52 are for all types     of conditions when the insulating materials specified are in contact with conductors.

### TABLE	52

TEMPERATURE LIMITS FOR  INSULATING

MATERIALS IN CONTACT WITH  CONDUCTORS

| Material | Temperature limit °C |
| --- | --- |
| PVC — V-75, V-90, V-90HT, HFI-75-TP and |  |
| HFI-90-TP |  |
| — up to and including 300 mm2 | 160 |
| — greater than 300 mm2 | 140 |
| Elastomer R-EP-90, R-CPE-90, R-HF-90, |  |
| R-CSP-90, R-HF-110, and R-E-110 | 250 |
| XLPE, X-90, X-HF-90 and X-HF-110 | 250 |
| Silicone rubber, R-S-150 | 350 |

    - Outer sheath and bedding materials   The temperature limits given in  Table 53    are for the outer sheath and bedding materials comprising a continuous screen/ sheath or a complete layer of armour wires. These temperatures are for materials where there is no electrical or other requirements necessary, i.e. screen/sheath/armour temperature limits  when in contact with the outer sheath materials but  thermally  separated  from  the  insulation by  layers of  suitable material of  sufficient thickness. If  thermal separation is  not provided, the temperature limits of  the insulation should be  used if  it  is  lower than that of the  sheath.

COPYRIGHT

91	AS/NZS 3008.1.2:1998

### TABLE	53

TEMPERATURE LIMITS FOR OUTER SHEATH AND BEDDING MATERIALS

| Material | Temperature limit °C |
| --- | --- |
| Thermoplastic | 200 |
| Polyethylene | 150 |
| High density polyetheylene | 180 |
| Polychloroprene, chlorosuphonated |  |
| polyethylene and similar | 200 |

    - Conductor and metallic sheath materials and components  The  temperature  limits specified in Table 54 apply to the conductor and metallic sheath materials and components.

NOTE: Limitations of materials in contact with these metals should also be considered.

### TABLE	54

TEMPERATURE LIMITS FOR CONDUCTOR AND METALLIC SHEATH MATERIALS AND COMPONENTS

| Metals | Condition | Temperature limit °C |
| --- | --- | --- |
| Copper and aluminium | Conductor only* | † |
|  | Welded joint | † |
|  | Exothermic welded joint | 250‡ |
|  | Soldered joint | 160 |
|  | Compression (mechanical deformation) joint | 250‡ |
|  | Mechanical (bolted) joint | § |
| Lead |  | 170 |
| Lead alloy |  | 200 |
| Steel |  | † |

*  Includes concentric neutral  conductors.

†  Limited by the material with which it is in    contact.

‡ Temperature of adjacent conductor; actual joint will be at a lower temperature.

§  Refer to manufacturer’s  recommendations.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	92

APPENDIX	A

## EXAMPLES OF THE SELECTION OF CABLES TO SATISFY CURRENT-CARRYING CAPACITY, VOLTAGE DROP AND SHORT-CIRCUIT PERFORMANCE REQUIREMENTS

(Informative)

### A1    EXAMPLE 1

A1.1 Problem An underground 1500 A three-phase circuit is to be made up of parallel circuits of 400 mm2 V-75 single-core insulated and sheathed copper cables. Determine the minimum number of active conductors required for each of the following forms of installation:

- All cables in one conduit or   duct.

- Each parallel circuit comprised of three cables in one conduit or duct.

- Each parallel circuit comprised of a trefoil group of single-way underground ducts.

- Each parallel circuit comprised of a trefoil group of three cables buried direct.

A1.2 Solution Assuming that the conditions specified in Clause  3.4  apply,  i.e.  soil  ambient temperature, thermal resistivity and depth of laying, the following methods would satisfy the load requirements if the voltage drop is    acceptable:

- Method A—single conduit or  duct

Current-carrying capacity of single 400 mm2 circuit = 561 A (Table 6, Column 16).

From the derating factors of Table 22, which vary according to the number of  enclosed circuits, it can be shown that five parallel circuits of 400 mm2 conductors,    as illustrated, are  required.

The current-carrying capacity of the arrangement is— 561 × 5 × 0.60 = 1683 A

- Method B—groups of conduits or  ducts

Current-carrying capacity of single 400 mm2 circuit = 561 A (Table 6, Column 16).

From the derating factors of Table 26(2) for  groups of  underground enclosures, it  can be shown that four conduits or ducts, each containing a circuit of 400 mm2 conductors and touching, as illustrated, are   required.

The current-carrying capacity of the arrangement is— 561 × 4 × 0.79 = 1772.8 A

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

93	AS/NZS 3008.1.2:1998

- Method C—trefoil groups of single-way underground   ducts

Current-carrying capacity of single 400 mm2 circuit = 616 A (Table 6, Column 18)

From the derating factors of Table 26(1) for  groups of  underground enclosures, it  can be shown that four trefoil groups of single-way underground ducts, each group representing a circuit of 400 mm2 conductors, as illustrated, are    required.

The current-carrying capacity of the arrangement— 616 × 4 × 0.74 = 1823.4 A

- Method D—trefoil groups of cable buried   direct

Current-carrying capacity of single 400 mm2 circuit = 649 A (Table 6, Column 14).

From the derating factors of Table 25(1) for groups of  single-core  cables  buried direct, it can be shown that three trefoil groups of single-core cables, each group representing a circuit of 400 mm2 conductors and spaced apart, as illustrated, are required.

The current-carrying capacity of the arrangement is— 649 × 3 × 0.87 = 1694 A

A1.3 Comparison of different methods Each of the  four  methods  of  installation described in Paragraph A1.2 provides a satisfactory solution to the circuit design problem where the number of 400 mm2 active conductors are to be kept to a minimum for a given installation method. However, in doing so the following factors which may determine the system to be selected are  highlighted:

- Number of cables	Method A leads to the largest number of   cables.

- Number of enclosures Method C requires twelve enclosures  (excluding  neutral)  whilst Method D requires  none.

- Size of enclosures The enclosures in Method C need only be sufficient  to accommodate one conductor; however, the single enclosure in Method A  will need    to be considerably  larger.

- Size of excavated trench Methods A, B  and  C  require  relatively  small  trench  widths in comparison to Method  D.

COPYRIGHT

AS/NZS 3008.1.2:1998	94

- Provision for additional load All  methods  have  provision  for  a  further  load increase of between 183 and 323 A. Methods A and D have the smallest margin of increased load capability.

The relative importance of these different factors for a particular installation will, in  general, determine the cable arrangement  selected.

### A2    EXAMPLE 2

A2.1	Problem	If 12 loaded single-core conductors are run through a wiring enclosure what derating factor should be  applied?

A2.2 Solution The applicable derating factors could be determined from Table 22. If three-phase circuits, 12/3 is 4 groups, i.e. 4 circuits, and a derating factor of 0.65 could be applied. If the circuits are single-phase, there would be 6 circuits and therefore a derating factor of 0.57 could be  applied.

Applying these derating factors for, say, V-75, 4 mm2 conductors, from Table  6  a  three-phase current-carrying capacity is 30 A  while  the  single-phase value  from  Table  3  is 34 A.

Using the three-phase approach, 30 × 0.65 = 19.5 A. Using the single-phase approach, 34 × 0.57 = 19.4    A.

Note that these methods result in approximately the same    answer.

### A3    EXAMPLE 3

A3.1 Problem A three-phase circuit is to supply a load of  125  A  per  phase.  It  is  proposed to use two V-75 four-core insulated and sheathed cables bunched together on a surface in a confined ceiling space where the ambient air temperature is 50°C.

Determine—

- the minimum conductor size;  and

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

the maximum route length of the circuit if a voltage drop of 3% is permitted on the circuit;

for both aluminium and copper  conductors.

A3.2    Solution    The solution is as  follows:

- Minimum cable size:

Derating factor for bunching = 0.8 (Table 22, Column    5)

Derating factor for 50°C ambient = 0.72 (Table 27(1), Column 9) Minimum current-carrying capacity of two parallel   cables—

or 108.5 A per  cable.

From Columns 4 and 5  of Table 12, the minimum size of  the two cables making up the circuit are—

Aluminium—50 mm2 Copper—35 mm2.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

95	AS/NZS 3008.1.2:1998

- Maximum route length:

With the same length and disposition of the two cables throughout the  circuit, balanced current flow between the parallel cables can be    expected.

Assuming worst case conditions of cable operating temperature and load power  factor, the simplified method of Clause 4.2 may be used to determine the maximum route length of the circuit (L), in metres, by substitution of  the 62.5 A  load current  for each cable and 3 % (12.0 V) permissible voltage drop in the following equation:

The values of Vc are obtained from Table 42 for copper and Table 45 for aluminium and result in the following maximum route   lengths:

Aluminium

Copper

### A4    EXAMPLE 4

A4.1 Problem Six four-core V-75 insulated and sheathed copper cables are arranged touching in a single horizontal row on a perforated cable tray for  the  supply  of  six identical 22 kW motors which have a  full-load current of 45 A per phase and are installed   at distances of 40 m, 55 m, 90 m, 135 m, 180 m  and 225 m  from the origin of the cable   tray. Determine the minimum conductor size if a voltage drop of 2.3% (10 V) is permitted for each cable.

A4.2 Solution The selection of conductor size in this instance must satisfy both the current-carrying capacity requirement, including the effect of  the  cables being  grouped, and the voltage drop  limitation.

The cable sizes required to satisfy the voltage drop restriction are assessed using  the  formula of Clause 4.2, the actual load current of 45 A, the permissible voltage drop, Vd,       of 10 V and the three-phase voltage drop figures of Table 42. The results of these calculations, the current-carrying capacity given in Table 12 and its ratio to the  load  current, are as  follows:

| Cable | Length m | Maximum Vc mV/A.m | Minimum cable size mm2 | Maximum current- carrying capacity A | Ratio of actual load current to max. current- carrying capacity of cable |
| --- | --- | --- | --- | --- | --- |
| A B C D E F | 40 55 90 135 180 225 | 5.56 4.04 2.47 1.65 1.23 0.98 | 10 10 16 25 35 50 | 58 58 78 104 125 154 | 0.78 0.78 0.58 0.43 0.36 0.29 |

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	96

Because of voltage drop limitations, cables C to F are substantially larger than required to meet the maximum current-carrying capacity requirements. As a result the contribution of these cables to the effects of mutual heating will be small; in the case of cables E and F, almost negligible.

An examination of the derating factors for groups of multicore cables on perforated trays given in Table 24 would indicate that a factor of 0.76 (Column 9) would apply if all six cables in the group were loaded to achieve  the  same  conductor  temperature.  Although these conditions do not exist for all cables in this example, the application of this factor    will give a conservative but practical solution, as    follows:

Minimum current-carrying capacity required of cables = Minimum cable size = 16 mm2 (Table 12, Column   4)

As expected, only cables A and B are affected and therefore the recommended minimum cable sizes for the cables A, B, C, D, E  and F  will be 16 mm2, 16 mm2, 16 mm2, 25 mm2,     35 mm2 and 50 mm2   respectively.

NOTE: The actual derating factor in this situation may be closer to 0.82, the derating factor for three cables on a tray, which allows for restricted ventilation to cables nested in the middle of others. Alternative arrangements of the cables, e.g. spacing cables A and B, which operate at a higher temperature, away from each other and others in the group, may also give rise to less onerous derating factors and smaller cable   sizes.

### A5    EXAMPLE 5

A5.1 Problem Five single-phase circuits of  two-core flat V-75 insulated and sheathed cables are fixed to a  wall. Where the continuous loading of the cables is assessed as 16,    20, 25, 32, and 40 amps, determine the minimum cable sizes required where the cables are   in one of the following  conditions:

- Condition A—spaced apart in a  single layer  in  accordance with  Clause 3.5.2.2(c) and Figure 1.

- Condition B—spaced apart in a single layer by a distance of one cable diameter between adjacent cables.

- Condition C—touching in a single  layer.

- Condition D—bunched together.

A5.2    Solution    The solution is as  follows:

- For installation condition A to avoid derating because of grouping, Clause 3.5.2.2(c) and Figure 1  require a  minimum vertical spacing between adjacent cables 6  times  the diameter of the largest cable in the   group.

- For condition B, the derating factor = 0.90 (Table 22, Column 8).

- For condition C, the derating factor = 0.73 (Table 22, Column 8).

- For condition D, the derating factor = 0.60 (Table 22, Column 8).

COPYRIGHT

97	AS/NZS 3008.1.2:1998

The minimum conductor sizes determined from Column 4 of Table 9 are as follows:

| Load A | Cable size, mm2 |  |  |  |
| --- | --- | --- | --- | --- |
|  | Spaced 6 diameters | Spaced 1 diameter | Touching single layer | Bunched |
| 16 | 1.0 | 1.5 | 2.5 | 2.5 |
| 20 | 1.5 | 2.5 | 2.5 | 4 |
| 25 | 2.5 | 2.5 | 4 | 6 |
| 32 | 4 | 4 | 6 | 10 |
| 40 | 6 | 6 | 10 | 10 |

### A6    EXAMPLE 6

A6.1 Problem A single-phase circuit is comprised of two 16 mm2 copper single-core sheathed cables with V-75 insulation installed unenclosed on  a  wall for the supply of  a      55 A resistive  load.

Determine which single-phase voltage drop values will apply when the cable is operating in—

- an ambient air temperature of 30°C;   or

- an ambient air temperature of  25°C.

A6.2  Solution   From Table 3  it will be noted that the cable current-carrying capacity of   this configuration is 82 A in an ambient air temperature of 30°C. Equation 4.4(1) may therefore be solved directly for cable operating temperature (0) where the ambient air temperature is 30°C but requires some correction to the rated  current  (IR) before application to an ambient air temperature of  25°C.  Appropriate  calculations  are  as follows:

- Ambient air temperature  30°C

0 = 50.2°C, say  60°C

The three-phase voltage drop for this cable configuration and operating temperature obtained from Table 41 is 2.32 mV/A.m. The single-phase value is then determined    in accordance with Clause  4.3.3(a).

Single-phase voltage drop value  =  1.155 ×  2.32

=  2.68 mV/A.m.

- Ambient air temperature  25°C

The correction factor for operation in a 25°C ambient air temperature is used to determine the maximum current which will give rise to the maximum operating temperature of 75°C.

Correction factor = 1.06 (from Table   27)

0 = 45.02°C, say  45°C

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	98

The three-phase voltage drop for this cable configuration and operating temperature obtained from Table 41 is 2.20 mV/A.m. The single-phase value is then determined    in accordance with Clause  4.3.3(a)—

Single-phase voltage drop value  =  1.155 ×  2.20

=  2.54 mV/A.m.

### A7    EXAMPLE 7

A7.1  Problem  A  three-phase  circuit  is comprised  of   3   ×   150   mm2   single-core copper V-75 sheathed active conductors and a 1 × 70 mm2 single-core  copper  V-75  sheathed neutral conductor bunched together in free air. Assuming an ambient air temperature of 30°C and the same length of 150 m for all conductors, determine the maximum voltage drop when the magnitude and phase angle of the currents in  the  respective active conductors are as  follows:

IA  = 195

IB  = 300

IC  = 230

0_°

1_2_0 °

2_4_0 °

A7.2  Solution   It is not necessary in this example to  take into account the load power  factor as the maximum voltage drop conditions are assumed where load power factor and cable power factor are equal. The voltage drop in each cable will then be equal to ILZc.

The 300 A load current in phase B is, according to Table 6, close to the maximum permissible for such an arrangement and  consequently  the  conductor  operating temperature may be assessed as 75°C for the application of Table 40 corresponding to a three-phase voltage drop of 0.305  mV/A.m.

The voltage drop on phase B conductor alone is    therefore—

= 300

1_2_0 ° × 150  ×

= 7.924

1_2_0 °

The current flowing in the neutral is    determined from the relationship—

IA + IB + IC + IN =  0

IA + IB + IC  =  195    0° +   300

1_2_0 ° + 230     24_0_°_

=  195 + (−150 + j259.8) + (−115 −   j199.2)A

=  −70 + j60.6

IN  =  70 − j60.6

=  92.6 _−4_0_._9_°    A

The operating temperature of the neutral may then be determined in  accordance  with  Clause 4.4 and the rated figure given in Table 6, i.e.

0 = 38.67°C, say 45°C allowing for contact with conductors operating at higher temperatures.

From Table 40 and a  conductor temperature of 45°C the three-phase voltage drop is given  as 0.537 mV/A.m.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT

99	AS/NZS 3008.1.2:1998

The voltage drop on the neutral conductor alone is    therefore—

=	4_0_._9_°          V × 150  ×

92.6 _−

= 4.306 _−4_0_._9_°       V

The maximum single-phase voltage drop is   therefore—

| Vd | = | VdB − VdN = 7.924 1_2_0 ° − 4.306 −_4 0_.9_° |
| --- | --- | --- |
|  | = = | −3.962 + j6.862 − 3.255 + j2.819 −7.217 + j9.681 |
|  | = | 12.08 1_2_6 .7_° V |

### A8    EXAMPLE 8

A8.1   Problem    Select the  minimum size  conductor based  on  thermal consideration, for  a copper cable with compression joints connected to a supply where protection is provided by an air circuit-breaker with a clearance time of 1 s and a breaking capacity of 10 kA.

Calculate the minimum conductor size for the following two types of cable:

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

PVC insulated.

- XLPE insulated.

A8.2    Solution    The solution is as  follows:

- PVC insulated    The following steps are  taken:

  - To find the value of constant (K) the initial conductor temperature and  the  final conductor temperature must be  known.

For PVC it is assumed that the initial operating  temperature  is  75°C  (for V-75, V-90 and V-90HT). From Table 52, and assuming that the cable  is smaller than 300 mm2, the final operating temperature can be selected  as  160°C. From Table 51 the value of K can be selected as 111 for a copper conductor.

  - As the circuit-breaker protecting the circuit is rated at 10 kA breaking capacity, we can assume a value of 10 000 A for I.

  - As the clearance time of the circuit-breaker is 1 s, it can be assumed that the value of t, which is the total time the fault current is flowing, is also 1 s.

  - Rearranging Equation in Clause 5.3 we   get—

Substituting the values for I, t and K, the minimum cross-section area is calculated as—

=  90.1 mm2

Therefore, the minimum cable size would be 95    mm2.

COPYRIGHT

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

AS/NZS 3008.1.2:1998	100

- XLPE  insulation	Using  the  same  process  as  in  Item  (a)  the  following  steps  are taken:

  - Initial operating temperature for XLPE insulation (assumed maximum) 90°C Final operating temperature from XLPE insulation (from Table 52) . . 250°C Value of constant (K) from  Table 51	143

(ii)	Value of short-circuit current (I) . . . . . . . . . . . . . . . . . . . . . . . . . 10 000 A (iii)	Value of time (t) is  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .  1 s

(iv)

= 69.9 mm2.

Therefore, the minimum cable size would be 70    mm2.

COPYRIGHT

101	AS/NZS 3008.1.2:1998

APPENDIX	B

## RECOMMENDED CIRCUIT CONFIGURATIONS FOR THE INSTALLATION OF SINGLE-CORE CABLES IN   PARALLEL

(Informative)

| Mode | Two-phase | Three-phase |
| --- | --- | --- |
| Two conductors per phase |  |  |
| Three conductors per phase | Not recommended |  |
| Four conductors per phase |  |  |

NOTES:

- Neutral conductors are to be located so as to not disturb the symmetry of the groups as illustrated.

- Non-symmetrical configuration may cause unequal distribution of current between  conductors.  Provision should be made to maintain the recommended configurations to avoid these problems.

--`,,,``,`,,``,,,,,`````,`,,`,,`-`-`,,`,,`,`,,`---

COPYRIGHT